## MAIN SHEET
DATE | TIME | TD REPORT NO. | TD REPEAT REF NO. | REPEAT COMPLAINTS | WTY ¦ AMC | CUSTOMER | BRANCH | LOCATION | FAILURE DETAILS | TECH 1 | TECH 2 | TIME IN | TIME OUT | Action taken | Others Details/ Spare parts needed | Technician Feedback | Status | Comments | Remarks
2026-01-01 | 8:44 | 120260001 | 120260001 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | CHEESE OR OLIVE CHILLER NOT COOLING / GLASSDOOR CHEESE CHILLER HIGH TEMP | RANDOLPH | OLIVER, FROILAN | 11:00 | 14:06 | LEAK FOUND AND ARRESTED, CHRAGDE REF / CONTROLLER ALARM RESTARTED AND UNIT RUNNING NORMAL | USED: R22-1, R404A-1, SILFOS ROD-2 |  | COMPLETED | WORK COMPLETED
2026-01-01 | 9:11 | 120260002 | 120260002 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | CHICKEN BREAST FREEZXER f#7 TEMP ISSUE | FROILAN | OLIVER | 10:20 | 10:43 | STARTING KIT CAPACITOR DAMAGE AND REPLACED. UNIT RUNNING NORMAL | USED: STARTING KIT CAPACITOR FROM BRANCH |  | COMPLETED | WORK COMPLETED
2026-01-01 | 13:00 | 120260003 | 120260003 | 1 | AMC | AD COOP/DEYAAR | MBZ | AUH | FREEZER F#22 HIGH TEMP | RANDOLPH | OLIVER, FROILAN | 15:00 | 16:41 | FOUND THE SOLENOID COIL DEFECTIVE FUNCTION, REPLACE THE CONNECTOR AND NOW UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-01 | 15:29 | 120260004 | 120260004 | 1 | AMC | CAREEM | JVT | DXB | FREEZER HIGH TEMP | SARAVANAN |  | 16:00 | 17:00 | CHARGED REF AND RESTARTED THE UNIT | USED: R404A-1CYL |  | COMPLETED | WORK COMPLETED | LEAK CHECK NEED TO DO
2026-01-01 | 14:00 | 120260005 | 1220250563 | 1 | AMC | AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | CHILLER CABINET REFRIGERANT CHARGING | MOHAMMED |  | 15:00 | 16:30 | CHARGED 3 CYL AND 2 CYLS KEPT IN STORE. UNIT WORKING NORMAL | USED: R404A-5CYLS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-01 |  | 120260006 | INSULATION WORK | 1 | AMC | AD COOP/DEYAAR | MBZ | AUH | INSULATION REPLACEMNET FOR THE FREEZER REF LINES | ROGER | GOVING, ZALAUDDIN |  |  | ALL INSULATION WORK DONE |  |  | COMPLETED | WORK COMPLETED
2026-01-01 | 22:00 | 120260007 | 120260005 | 2 | AMC | GMG | SAHARA MALL | SHJ | FREEZER AND CHILLER CABINET DISMANTLING | DENNIS, MUTHUKUMAR | SUDHEESH, ABIJITH | 22:00 | 6:00 | FREEZER CABINET AND CHILELR CABINET DISMANTLED AND WRAPPING COMPLETED |  |  | COMPLETED | WORK COMPLETED
2026-01-01 | 8:36 | 120260008 | 120260006 | 1 | AMC | NESTO | AJJ | AJM | ICE CREAM FREEZER TEMP ISSUE | TALIB |  | 9:20 | 11:45 | LEAK FOUND IN THE SUCTION VALVE IN COMPRESSOR AND TOP UP THE GAS IN FREEZER AND CLOSE VALVE CAP PROPERLY | USED: R22-1CYL BY TD / NEED: SUCTION VALVE 1 1/8-1NO, R22-2CYL, BLUE ROD-3NOS, COPPER ROD-3NOS |  | COMPLETED | WORK COMPLETED
2026-01-01 | 9:09 | 120260009 | 120260007 | 1 | AMC | NESTO | AJG | AJM | FREEZER COLD ROOM NOT WORKING | VIGNESH | SELVAN | 18:15 | 19:00 | REPAIRED THE DOOR LIMIT SWITCH AND NOW OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-01 | 12:21 | 120260010 | 120260008 | 1 | AMC | TCS | SAFA PARK | DXB | DISPLAY FREEZER NOT WORKING | MOHAMMED |  | 13:15 | 13:45 | ALL FREEZER WORKING NOMAL | NEED: DISPLAY THERMOMETER - 3NOS |  | ATTENDED | NEED MATERIAL
2026-01-01 | 19:15 | 120260011 | 120260009 | 1 | AMC | TCS | SHOROOQ | DXB | BEVERAGE, DAIRY, F&v AND BAKERY CHILLER IS NOT FUNCTIONING | VIGNESH | SELVAN | 19:30 | 21:30 | RESET THE ELCB AND NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-01 | 9:15 | 120260012 |  | 0 | AMC | ENOC | 1205 | AJM | CHILLER TEMP SHOWING NEGATIVE, NO COOLING | RACEL | [6 empty] | COMPLETED
2026-01-01 | 13:36 | 120260013 | 7100288853 | 2 | AMC | ENOC | 4007 | DXB | CHILLER #2 | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 2JAN26
2026-01-01 | 13:36 | 120260014 | 7100288888 | 1 | AMC | ENOC | 1074 | DXB | BED FREEZER CREATE ICE FORMATION | SADAM |  | 17:45 | 18:45 | ITS NOT UNDER OUR SCOPE |  |  | ATTENDED | NOT OUR SCOPE
2026-01-01 | 13:36 | 120260015 | 7100288904 | 2 | AMC | ENOC | 509 | FUJ | OPEN CHILLER LIGHT DETACHED | AHSAN | TALIB | [5 empty] | ATTENDED
2026-01-01 | 13:36 | 120260016 | 7100288910 | 1 | AMC | ENOC | 1099 | DXB | WALKIN FREEZER BREAKDOWN | SARAVANAN |  | 13:15 | 15:00 | RESET THE SYSTEM, MOTOR PROTECTOR COMMENT NOT WORKING. NEED TO REPLACE | NEED: MOTOR PROTECTOR-1 |  | ATTENDED | NEED MATERIAL
2026-01-01 | 13:36 | 120260017 | 7100288935 | 1 | AMC | ENOC | 1029 | DXB | PRONTO VERTICAL CHILLER | SARAVANAN |  | 17:30 | 18:00 | TOP UP GAS AND NOW UNIT WORKING NORMAL, LEAK NOT FOUND |  |  | COMPLETED | WORK COMPLETED
2026-01-01 | 10:45 | 120260018 | 120260010 | 1 | AMC | ADNOC | 634 | SHJ | HOT DOG GRILLER NOT WORKING | ALLAN | WILLIAM | 22:45 | 22:46 | NOT TO USE, NEED TO REPLACE |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 10:11 | 120260019 | 7100288833 | 1 | AMC | ENOC | 1027 | DXB | OPEN CHILLER NOISE ISSUE | SADAM |  | 14:00 | 15:20 | REPLACE THE EVP FAN MOTOR AND OPEN CHILLER RUNNING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 10:11 | 120260020 | 7100289009 | 1 | AMC | ENOC | 1019 | DXB | HALOGEN LIGHT NOT WORKING | SADAM |  |  |  | NOT OUR SCOPE |  |  | ATTENDED | ATTENDED ON 3JAN26
2026-01-02 | 8:56 | 120260021 | 7100288853 | 2 | AMC | ENOC | 4007 | DXB | CHILLER #2 | SARAVANAN |  | 10:30 | 14:10 | NEED TO REPLACE FLOAT SWITCH | NEED: 220V FLOAT SWITCH-1NO |  | ATTENDED | NEED MATERIAL
2026-01-02 | 8:56 | 120260022 | 7100288332 | 1 | AMC | ENOC | 4007 | DXB | CHILLER #1 LIGHT NOT WORKING AND HIGH TEMP | SARAVANAN |  | 10:30 | 14:10 | STARTER LOOSE CONNECTION REFIXED, OLD FAN MOTOR REPLACED. NOW WORKING NORMAL | USED: 16W FAN MOTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-02 | 15:01 | 120260023 | 7100288904 | 2 | AMC | ENOC | 509 | FUJ | OPEN CHILLER LIGHT DETACHED | TALIB | AHSAN | [5 empty] | ATTENDED
2026-01-02 | 15:24 | 120260024 |  | 0 | AMC | ENOC | 1011 | DXB | OPEN CHILLER NOT WORKING | MOHAMMED |  | 19:00 | 19:15 | NEED TO REPLACE THE TAMP THERMOMETER | NEED: TEMP THERMOMETER-1 |  | ATTENDED | NEED MATERIAL
2026-01-02 | 9:21 | 120260025 | 120260011 | 2 | AMC | TCS | DEC MARINA | DXB | BACK STORE FREEZER TEMP ISSUE / ICE CREAM FREEZER CABINET WATER LEAK | SARAVANAN |  | 16:00 | 17:30 | FIXED THE DOOR LIMIT SWITCH PROPERLY AND UNIT WORKING NORMAL / ICE CREAM FREEZER NEED TO FIX FAN MOTOR DUE TO HUMIDITY ISSUE | NEED: 120*120CM FAN MOTOR-5NOS, 1.5MM*3C WIRE-5MTR, WIRE CONNECTOR-2NOS |  | COMPLETED | WORK COMPLETED | ON 10JAN26
2026-01-02 | 12:38 | 120260026 | 120260012 | 1 | AMC | TCS | GREENS | DXB | CHILLER WATER LEAK | SADAM |  | 23:15 | 1:15 | CLEANED THE DRAIN LINE AND SAME ISSUE NEED TO CLEAN THE DRAIN AND DRAIN LINE |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 16:08 | 120260027 | 120260013 | 1 | AMC | TCS | LE GRAND | DXB | UNIT IN CONTINOUS DEFROST | SADAM |  | 18:45 | 19:45 | COMPRESSOR DEFECTIVE NEED TO REPLACE | NEED: EMBRACO (NT6226GK)-1NO, R404A-1, DCL032 FILTER DRIER-1, NITROGEN-1 |  | ATTENDED | NEED MATERIAL
2026-01-02 | 17:25 | 120260028 | 120260014 | 1 | AMC | TCS | JVC MANHATTAN | DXB | FREEZER WATER LEAKAGE | SADAM |  | 21:15 | 22:45 | REPLACED DRAIN HEATER HOSE TO ANOTHER DRAIN, DRAIN PAN DAMAGE NEED TO REPLACE | NEED: DRAIN PAN (29CM-LENGTH, 10CM WIDTH, 10CM HEIGHT)-1NO |  | ATTENDED | NEED MATERIAL
2026-01-02 | 17:41 | 120260029 | 7100289140 | 2 | AMC | TCS | 1057 | DXB | VERTICAL FREEZER ICE FORMATION | SADAM |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 3JAN26
2026-01-02 | 17:51 | 120260030 | 7100286363 | 1 | AMC | ENOC | 1041 | DXB | WALKIN CHILLER INSIDE LIGHT BUSTED | RAJESH |  | 18:40 | 19:30 | NEW LED SET FIXED AND REWIRING DONE | USED: LED WEATHERPROOF LIGHT -1. TOTAL LENGTH(238CM) BY TD |  | COMPLETED | WORK COMPLETED
2026-01-02 | 23:21 | 120260031 |  | 0 | AMC | ENOC | 1094 | DXB | WALKIN FREEZER HIGH TEMP | VIGNESH | SELVAN | 12:05 | 12:40 | CHECKED UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 8:21 | 120260032 | 120260016 | 1 | AMC | BANIYAS COOP | SARAB | AUH | BUTCHERY CHILLER TRIPPING ISSUE | RANDOLPH | TROVEE | 9:50 | 10:10 | UNIT WORKING NORMAL, CHECKED ALL THE MANUAL DEFROST NORMAL PARMETERS |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 8:24 | 120260033 | 120260017 | 1 | AMC | PASONS | 28 | FUJ | CHILLER HIGH TEMP AND ALARM | AHSAN | TALIB | 13:20 | 16:00 | LIQUID RECEIVER AREA GAS LEAK ARRESTED AND VACUUM THE GAS AND CHARGE NEW | USED: R22-1CYL |  | COMPLETED | WORK COMPLETED
2026-01-02 | 12:40 | 120260034 | 120260018 | 1 | AMC | GRANDIOSE | AL BUSTAN | AUH | CHILLER HIGH TEMP | FROILAN | WILLIAM | 20:37 | 21:39 | NEED TO REPLACE DIXELL CONTROLLER, AND CONTACTOR | NEED: DIXELL CONTROLLER-1, CONTACTOR LC1D25-1 |  | ATTENDED | NEED MATERIAL
2026-01-02 | 12:54 | 120260035 | 120260019 | 1 | AMC | AL AIN COOP | AL MANASIR | AL AIN | FREEZER GLASS DOOR ISSUE, OPENS AUTOMATICALLY | VIGNESH | SELVAN | 20:40 | 21:30 | REPAIR THE FREEZER DOOR AND NOW AUTOMATICALLY CLOSING |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 13:37 | 120260036 | 120260020 | 2 | AMC | BAQER MOHEBI | WAREHOUSE | DXB | CHILLER UNITY POWER TRIPPING | SHAFI | MOHAMMED |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 3JAN26
2026-01-02 | 17:23 | 120260037 | 120260021 | 1 | AMC | CAREEM | JLT | DXB | F&V OPEN CHILLER OT WORKING | SADAM |  | 20:15 | 21:00 | PLUG POINT FOR PUWER SUPPLY FIXED PROPERLY |  |  | COMPLETED | WORK COMPLETED
2026-01-02 |  | 120260038 | 120260022 | 1 | AMC | CAREEM | JVT | DXB | LEAK CHECK AND ARRESTING | SHAFI | MOHAMMED, MUSTAFA |  |  | LEAK FOUND IN LIQUID RECIVER AREA AND ARRESTED, UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 8:42 | 120260039 | 120260023 | 1 | AMC | NESTO | FUJAIRAH MALL | FUJ | HOT FOOD SECTION EVP GAS LEKAGE / BUTCHERY COLD ROOM SLIDING DOOR STUCK | AHSAN | TALIB | 10:50 | 12:40 | FIXED THE LEAK AND VACUUM THE EVP AND START THE UNIT AMD CHNAGED THE CONTROLLER SETTING / SLIDING DOOR STUCK PROBLEM AND DOOR GUIDE WHEEL DAMAGE, NEED TO BE REMOVE THE DOOR FRAME AND NEED TO INSTALL PROPERLY | NEED: DOOR GUIDE WHEEL-1, NYLON TENSION ROD-5NOS |  | ATTENDED | NEED MATERIAL
2026-01-02 | 8:52 | 120260040 | 120260024 | 1 | AMC | NESTO | AL FAHIDI | DXB | CHILLER SHUTDOWN | MOHAMMED |  | 11:00 | 12:30 | REMOVED THE DRAIN LINE BLOCK AND ALL FAN MOTOR DRY BY BLOWER AND REFI STARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 9:29 | 120260041 | 120260025 | 1 | AMC | NESTO | AL AIN CENTER | AL AIN | BAKERY SECTION CHILLER NOT WORKING | VIGNESH | SELVAN | 19:15 | 20:10 | FOUND DRAIN PAN HEATER DEFECTIVE AND UNIT WORKING NORMAL | NEED: DRAIN PAN HEATER-1NO |  | ATTENDED | NEED MATERIAL
2026-01-02 | 11:05 | 120260042 | 120260026 | 1 | AMC | NESTO | AJC | AJM | ALL FREEZERS HIGH TEMP | GOVIND | ZALAUDDIN | 22:00 | 6:30 | FREEZER #2 & #3 EVP COIL FULL WATER SERVICE DONE AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 13:44 | 120260043 | 120260027 | 1 | AMC | NESTO | AJE | AJM | ISLAND FREEZER HIGH TEMP | VIGNESH | SELVAN | 14:55 | 16:30 | GAS LEAK ARRESTED AND TOP UP GAS UNIT WORKING NORMAL | USED: R404A-1 BY NESTO |  | COMPLETED | WORK COMPLETED
2026-01-02 | 20:19 | 120260044 | 120260028 | 1 | AMC | NESTO | FUJAIRAH MALL | FUJ | ALL FREEZER NO COOLING | RACEL |  | 20:09 | 5:15 | DEEP ICE FORMATION CLENAED THE COIL FOR 8 CABINETS IN ISLAND FREEZER. CHECK THE DEFROST SETTING AND TIMING WORKING NORMAL | NEED: 1 1/2" CLAMP-5NOS, 1" CLAMP-5NOS |  | ATTENDED | NEED MATERIAL
2026-01-02 | 11:17 | 120260045 | 120260029 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | NEED TO CLEAN THE UNIT | FROILAN | WILLIAM | 23:55 | 24:21 | CLEANED OF DUSTY EVP FAN BLADE GRILLS |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 18:03 | 120260046 | 120260030 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | CHEESE CHILLER HIGH TEMP | FROILAN | WILLIAM | 23:55 | 24:21 | OLIVE CHEESE CHILLER DISPLAY REPLACEMENT OF UNITS, UNIT UNREPAIRABLE |  |  | COMPLETED | WORK COMPLETED
2026-01-02 | 21:30 | 120260047 | 120260031 | 1 | AMC | AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | BAKERY SECTION CHILLER HIGH TEMP | VIGNESH | SELVAN | 14:15 | 15:00 | FOUND DEFCETIVE COMPRESSOR | NEED: COMPRESSOR (TECUMSEH)-1, R134A-1, 3/8 FILTER DYER-1, BRAZING ROD-5NOS, CHARGING PIN 1/4-1NO |  | ATTENDED | NEED MATERIAL
2026-01-02 | 13:35 | 120260048 | 120260015 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | F&V COLD ROOM CHILLER - REPLACE OF CDU AND EVP | RANDOLPH, TROVEE, OLIVER | ALL AIN, FROILAN, WILLIAM | 13:35 | 24:45 | OLD DEFECTIVE CDU DISMATLED AND INSTALLED NEW, INSTALL THE REF CONTROLLER AND ASSEMBLE THE ELECTRICAL CONNECTIONS CHARGE THE REF AND ENERGIZE THE UNIT | VARIOUS MATERIAL USED |  | COMPLETED | WORK COMPLETED
2026-01-02 |  | 120260049 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON | [6 empty] | ATTENDED
2026-01-03 | 6:59 | 120260050 |  | 0 | AMC | ENOC | 1041 | DXB | OPEN CHILLER HIGH TEMP | SHAFI | MOHAMMED | 10:30 | 11:30 | RESET THE RESTORE THE PARAMETER SETTING AND RESTART THE UNIT |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 7:43 | 120260051 | 7100289100 | 2 | AMC | ENOC | 508 | FUJ | OPEN CHILLER TRIPPING ISSUE | VIGNESH | SELVAN | 24:00 | 24:45 | DEFECTIVE COMPRESSOR | NEED: COMPRESSOR (NJ9238GK)-1, R404A-1, FILTER DRIER 1/2 SOLDER-1, BRAZING ROD-2NOS |  | COMPLETED | WORK COMPLETED
2026-01-03 | 11:12 | 120260052 | 7100289101 | 1 | AMC | ENOC | 1062 | DXB | PRONTO FREEZER NOT WORKING | SHAFI | MOHAMMED | 12:04 | 14:15 | REPLACED COND FAN MOTOR AND UNIT WORKING NORMAL | USED: FAN MOTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-03 | 11:12 | 120260053 | 7100289130 | 2 | AMC | ENOC | 1033 | DXB | WALKIN FREEZER ICE FORMATION | SHAFI | MUSTAFA | 12:00 | 12:15 | WALKIN FREEZER BACK DOOR FRAME PLATIC CURTAIN FULL OF ICE AND BOTTOM GASKET DAMAGE, NEED TO REPLACE | NEED: BOTTOE GASKET-2NO |  | COMPLETED | WORK COMPLETED | ON 15JAN25
2026-01-03 | 11:12 | 120260054 | 7100289155 | 1 | AMC | ENOC | 509 | FUJ | ICE FORMATION ON CHILLER COMPRESSOR | VIGNESH | SELVAN | 22:30 | 23:30 | CHECK THE CHILLER WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 11:12 | 120260055 | 7100289175 | 1 | AMC | ENOC | 1062 | DXB | PRONTO VERTICAL CHILLER | SHAFI | MOHAMMED | 12:04 | 11:30 | REPROCESS THE SYSTEM BY REMOVED THE EXISTING GAS AND NEED TO REPLACE DIGITAL CONTROLLER | USED: R134A-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-03 | 13:54 | 120260056 |  | 0 | AMC | ENOC | 1099 | DXB | WALKIN FREEZER SHUTDOWN | SHAFI | MOHAMMED | 15:00 | 15:30 | REPLACED NEW TIME DELAY, RESTART THE UNIT AND WORKING NORMAL | USED: DELAY TIMER-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-03 | 7:44 | 120260057 | 120260020 | 2 | AMC | BAQER MOHEBI | WAREHOUSE | DXB | CHILLER UNITY POWER TRIPPING | SHAFI | MOHAMMED | 9:00 | 10:00 | COMPRESSOR MECHANICALLY DEFECTIVE | NEED: COMPRESSOR(4PES-15.2-40P) - 1NO, HP LP SWITCH, HP LP HOSE-1 EACH |  | ATTENDED | NEED MATERIAL
2026-01-03 | 9:02 | 120260058 | 120260032 | 1 | AMC | BADIA FARMS | AL QUOZ | DXB | COMPRESSOR REMOVAL BY CRANE | SARAVANAN |  |  |  | COMPRESSOR PULL OUT DONE AND TAKEN BY REDDEX TEAM |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 9:30 | 120260059 | 120260033 | 1 | AMC | PASONS | 28 | FUJ | CHILLER HIGH TEMP, SAME ISSUE | VIGNESH | SELVAN | 18:05 | 22:00 | FOUND PRESSURE SWITCH DEFECTIVE AND REPLACED AND UNIT WORKING NORMAL | USED: HP LP SWITCH KP15-1 BY TD |  | COMPLETED | WORK COMPLETED | REPEAT COMPLAINT
2026-01-03 | 9:55 | 120260060 | 120260034 | 2 | AMC | HOP | JEBAL ALI | DXB | COLD ROOM ICE FORMATION | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 5JAN26
2026-01-03 | 11:55 | 120260061 | 1220250492 | 1 | WTY | CAREEM | BANIYAS | AUH | WATER PUMP LEAK | RANDOLPH | TROVEE | 11:55 | 15:30 | DRAIN HOSE PINCHED AND DRAIN HOSE DISMANTLE AND REPIPEN THE PINCH |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 17:30 | 120260062 | 120260035 | 1 | WTY | CAREEM | ARABIAN CENTER | DXB | COLD ROOM FREEZER HIGH TEMP NOT ABOVE THAN -14 | AHSAN | MUTHUKUMAR | 19:30 | 23:00 | REMOVED EVP ICE AND CHANGED THE CONTROLLER SETTING AND CHANGED COIL SENSOR LOCATION |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 12:47 | 120260063 | 120260036 | 1 | AMC | NESTO | AJC | AJM | ISLAND FREEZER HIGH TEMP | ROGER | GOVIND, ZALAUDDIN | 4:00 | 5:40 | ARREST THE LEAK AND CHARGED THE REF AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 24:00 | 120260064 | 120260005 | 2 | AMC | GMG | SAHARA MALL | SHJ | CABINETS SHIFTING | ROGER, GOVIND | ZALAUDDIN, MUSTAFA, SHAHABUDDIN | 24:00 | 3:15 | PULL OUT THE 5 CABINETS AND LOADED IN THE VEHICLE AND TRANFERED TO ASWAQ WAREHOUSE |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 7:00 | 120260065 |  | 0 | AMC | ENOC | 4016 | DXB | REPLACEMENT OF COMPRESSOR OF CHILLER#3 | SABITH ALI | SHAFI | 7:00 | 22:20 | REPLECED THE COMPRESSOR AND FILTER DRIER. REPROCESS DONE | USEd: COMPRESSOR-1, FILTER DRIER 1/4-1, NITROGEN-1, R404A-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-03 | 13:00 | 120260066 |  | 0 | AMC | ENOC | 1052 | DXB | UINSULATION OF DIGITAL THERMOMETER IN OPEN CHILLER CABINET | SABITH ALI | BIJU, LORIMER | 13:00 | 13:20 | REPLACED THE DIGITAL THERMOMETER AND UNIT WORKING NORMAL | USED: DIGITAL THERMOMETER-1NO |  | COMPLETED | WORK COMPLETED
2026-01-03 | 14:05 | 120260067 |  | 0 | AMC | ENOC | 1101 | SHJ | DIGITAL THERMOMETER INSTALLATION | SABITH ALI | BIJU, LORIMER | 14:05 | 14:20 | REPLACED OPEN CHILLER CABINET | USED: DIGITAL THEMOMETER-1 |  | COMPLETED | WORK COMPLETED
2026-01-03 | 15:17 | 120260068 |  | 0 | AMC | ENOC | 1074 | DXB | WALKIN FREEZER HIGH TEMP AND DEFROST TIMING ISSUE | SHAFI | MOHAMMED |  |  | ADJUST THE LP SWITCH AND CALIBRATED CHANGEB THE DEFROST SCHEDULE AS PER THE LIST |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 17:30 | 120260069 | 7100288387 | 1 | AMC | ENOC | 1081 | DXB | WALKIN FREEZER DUST WAS FALLING IN ITEMS | SHAFI | MOHAMMED | 17:30 | 18:00 | NEED TO REPKACE THE EVP UNIT | NEED: EVP UNITS-2 |  | ATTENDED | NEED MATERIAL
2026-01-03 | 18:00 | 120260070 |  | 0 | AMC | ENOC | ZOOM4016 | DXB | OPEN CHILLER NOISE AND HIGH TEMP | SARAVANAN | SADAM | 18:00 | 19:00 | CONDENSATION SIR NOT PROPERLY AND FULL DAMAGE IN THE DUCT AREA |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 19:35 | 120260071 | 7100289140 | 2 | AMC | ENOC | 1057 | DXB | VERTICAL FREEZER ICE FORMATION | SADAM |  | 19:35 | 20:15 | DOOR HINGES SET DAMAGE | NEED: DOOR HINGES-2 |  | ATTENDED | NEED MATERIAL
2026-01-03 | 13:52 | 120260072 | 120260037 | 1 | AMC | AD COOP/DEYAAR | MBZ | AUH | FREEZER HIGH TEMP | OLIVER | WILLIAM | 14:57 | 15:32 | DOOR SIDE NOT CLOSED PROPELY AND EVP ICE BUILD UP AND MANUAL DERFROST THE ICE. UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 18:52 | 120260073 | 120260038 | 1 | AMC | AD COOP/DEYAAR | AD MALL | AUH | DAIRY CHILLER WATER LEAK | OLIVER |  | 20:22 | 21:10 | FOUND OVERFLOW AND FLOOR DRAIN LINE NOT CLEANED OUT |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 21:05 | 120260074 | 120260039 | 1 | AMC | ADNOC | 885 | FUJ | ICE MACHINE NOT WORKING | VIGNESH | SELVAN | 1:25 | 2:30 | CLENAED THE CONDENSER AND RESTARTED UNIT WORKING NROMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 10:13 | 120260075 | 120260040 | 1 | AMC | TCS | ROVE DOWNTOWN | DXB | CHILLER WATER LEAK | SARAVANAN |  | 16:15 | 17:00 | DRAIN BLOCK RECTIFIED AND OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 10:13 | 120260076 | 120260041 | 1 | AMC | TCS | FALCON KHALIDIYA | AUH | COLD ROOM DOOR ICE FORMATION | RANDOLPH | TROVEE | 16:50 | 17:00 | REMOVED THE ICE FORMATION AT THE DOOR AREA OD FREEZER COLD ROOM |  |  | COMPLETED | WORK COMPLETED
2026-01-03 | 21;24:00 | 120260077 | 120260042 | 1 | AMC | TCS | ROVE CITY CENTER | DXB | CHILLER HIGH TEMP | SADAM |  | 22:15 | 24:00 | NEED TO DO LEAK TEST | NEED: R404A-1, NITROGEN-1, FILTER DRIER FLARE 3/8-1, PT1000 SENSOR-2 |  | ATTENDED | NEED MATERIAL
2026-01-03 | 21:00 | 120260078 | 1220250434 | 1 | AMC | TCS | BAY SQUARE | DXB | PORK SECTION CHILLER 1 LIGHT NOT WORKING | SADAM |  | 21:00 | 021:45:00 | LAMP FUSE NEED TO REPLACE | NEED: 24V T5 FITTING-3NOS |  | ATTENDED | NEED MATERIAL
2026-01-03 |  | 120260079 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON | [6 empty] | COMPLETED
2026-01-04 | 7:43 | 120260080 | 120260043 | 1 | AMC | TCS | LAKES | DXB | PORK SECTION CHILLER HIGH TEMP | SHAFI | MOHAMMED | 10:00 | 12:20 | REMOVE THE PRIMARY COIL AND NEW PRIMARY COIL AND LEAK TEST AND WORKING NORMAL | 3/8 COPPER PIPE-5MTR, R404A-1, BLUE ROD-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-04 | 7:45 | 120260081 | 120260044 | 1 | AMC | TCS | JULPHAR TOWER | RAK | FREEZER CABINET HIGH TEMP | SARAVANAN | MUTHUKUMAR | 14:30 | 18:10 | NEED TO DRAIN PIPE ALTERNATION AND FULL ICE REMOVED THE COIL WATER SERVICE AND WORKING NORMAL | NEED: 1 1/4" PVC PIPE-3MTR, 1 1/4" COUPLING-3NOS, 1 1/4" T JOINT-2NOS, 1 1/4" ELBOW-4NOS, 1 1/4" DUMMY-1NO, PVC GLUE-1 |  | ATTENDED | NEED MATERIAL
2026-01-04 | 9:09 | 120260082 | 120260045 | 1 | AMC | TCS | KHALIDIYA | AUH | F&V NOT WOKRING | RANDOLPH | TROVEE | 11:20 | 12:00 | LEAK TEST THE SYSTEM AND NOT FOUND AND CHARGED ADDITIONALLY CHARGED | USED: R404A-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-04 | 12:59 | 120260083 | 120260046 | 1 | AMC | TCS | JVC MANHATTAN | DXB | BAKERY CHILELR WATER LEAK | RACEL | ROGER | 23:59 | 2:10 | DRAINAGE PIPE IMPROVISED CABINET FLOOR DRAIN. NO WATER LEAK BUT NEED CHANGE, FULL SET FLOOR DRAIN AND PIPE AND UNIT NO WATER LEAK | NEED: FLOOR DRAIN 1" INCH-2NOS, 1" T PIPE-5NOS, ELBOW 1" INCH-4NOS, END CAP 1"-1, PVC GLUE-1NOS |  | ATTENDED | NEED MATERIAL
2026-01-04 | 17:42 | 120260084 | 120260047 | 1 | AMC | TCS | AL RAIS | DXB | DISPLAY FREEZER AND FREEZER COLD ROOM ICE FORMATION | RACEL | ROGER | 19:24 | 23:10 | MANUAL DEFROST IN COLD ROOM FREEZER AND REMOVED ICE FORMATION. COLD ROOM NOW WORKING. FOUND COMMUNICATION CABLE IS NOT WORKING AND REMOVED THE ICE FORMATION | NEED: DANFOSS MANUAL THERMOSTAT PLUS AND MINUS RANGE-1NO |  | ATTENDED | NEED MATERIAL
2026-01-04 | 10:27 | 120260085 | 120260048 | 2 | AMC | NESTO | AJG | AJM | CHILLER LIGHT NOT WORKING | AHSAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 5JAN26
2026-01-04 | 23:05 | 120260086 | 120260049 | 3 | AMC | NESTO | AJF | AJM | WATER LEAK IN THE FREEZER | VIGNESH | SELVAN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 4JAN26
2026-01-04 | 7:47 | 120260087 | 120260050 | 2 | AMC | BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILELR NO COOLING / COLD ROOM CHILELR NOT WORKING | SARAVANAN | MUTHUKUMAR | 10:15 | 12:05 | COMPRESSOR GOT DEFECTIVE / WATER DRIP IN THE CONNECTOR EVP AND MAIN POWER OFF AND UNIT WORKING NORMAL | NEED: COMPRESSOR (SC15MLX)-1, R404A-1, 1/4 FILTER DRIER SOLDER-1, NITROGEN-1, 16W FAN MOTOR-1 |  | COMPLETED | WORK COMPLETED | ON 14JAN26
2026-01-04 | 12:16 | 120260088 | 120260051 | 1 | AMC | ANSAR | KARAMA | SHJ | COMBI FREEZER NOT WORKING | SHAFI | MOHAMMED | 13:15 | 14:30 | MANUALLY DEFROST THE TEMP OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-04 | 14:03 | 120260089 | 120260052 | 1 | AMC | BAQER MOHEBI | SATWA | DXB | FAN MOTOR NOISE ISSUE | SHAFI | MUSTAFA | 15:00 | 16:30 | REPLACED NEW CONDENSING FAN MOTOR AND RESTART THE UNIT | USED: FAN MOTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-04 | 17:03 | 120260090 | 120260053 | 2 | AMC | CAREEM | BANIYAS | DXB | WATER IN THE COLD ROOM PUMP | RANDOLPH | TROVEE | 20:20 | 20:45 | FOUND OUT MALFUNCTION WATER PUMP AND DRAIN PAN REMOVED | NEED: CONDENSATE PUMP (PC125A)-1NO |  | COMPLETED | WORK COMPLETED | ON 8JAN26
2026-01-04 | 23:40 | 120260091 | 120260054 | 1 | AMC | LULU | AL QUAA | AUH | WATER LEAK IN FRUIT CHILLER | TALIB |  | 23:40 | 14:10 | CLEAR THE DRAIN LINE AND DRAIN PAN TRAY AND BOTH SIDE AND CHILLER WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-04 | 18:37 | 120260092 |  | 0 | AMC | ENOC | 1142 | SHJ | WALKIN FREEZER WATER LEAK | RACEL | ROGER | 2:46 | 5:15 | REMOVE THE RUBBER INSULATION AND REPAIR THE LEAK. WRAPPED WITH CABLE TIE. UNIT WORKING WELL |  |  | COMPLETED | WORK COMPLETED
2026-01-04 | 18:45 | 120260093 | 7100288062 | 1 | AMC | ENOC | 1401 | DXB | OLD FREEZER NEED TO REPAIR | SARAVANAN | MUTHUKUMAR | 18:45 | 19:15 | TOP SLIDING DOOR POOR CONDITION AND NO HAVE GASKET, COMPRESSOR ABNORMAL SOUND | BETTER CHANGE THE NEW BED FREEZER UNIT |  | COMPLETED | WORK COMPLETED
2026-01-04 | 7:56 | 120260094 | 120260055 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | JUICE AND YOGHURT CHILLER HIGH TEMP | RANDOLPH | TROVEE | 17:24 | 19:00 | ADJUST THE TEMP SETPOINT AND ADITIONAL CHARGED REF | USED: R22 BY BRANCH |  | COMPLETED | WORK COMPLETED
2026-01-04 | 9:36 | 120260095 | 120260056 | 2 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | CHILLER AREA TEMP HIGH | RANDOLPH | TROVEE | 13:00 | 13:20 | FOUND UNDERCHARGE OF REF, DUE TO LEAK IN OLIVE ANDN CHEESE CHILLER EVP COIL LEAK | NEED: R404A-10CYLS |  | COMPLETED | WORK COMPLETED
2026-01-04 | 10:00 | 120260096 | 120260057 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | ICE CREAM FREEZER TEMP ISSUE | RANDOLPH | TROVEE | 14:00 | 16:00 | REPLACED THE FAN MOTOR AND DECLOGGED THE WATER LEAK AND WORKING NROMAL | USED: FAN MOTOR-1 |  | COMPLETED | WORK COMPLETED
2026-01-04 | 18:25 | 120260097 | 120260058 | 1 | AMC | AD COOP/DEYAAR | SPAR OMEGA | AUH | COLD DRINK CHILLER NOT WORKING | RANDOLPH | TROVEE | 19:25 | 20:00 | REMOVED THE STAGANT WATER AND DISCONNECT THE GROUNDED FAN MOTOR AND START TH UNIT | NEED: 10-20W FAN MOTOR-1NO |  | ATTENDED | NEED MATERIAL
2026-01-04 | 21:22 | 120260098 | 120260056 | 2 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | PLUS RANGE SYSTEM REF CHARGING | RANDOLPH | TROVEE | 21:22 | 24:00 | CHARGED THE REF FOR THE PLUS RANGE UNIT ONE BY ONE GRADUALLY, NOW UNIT WORKING NORMAL | USED: R404A-10CYLS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-05 | 8:28 | 120260099 | 120260059 | 1 | AMC | NESTO | AJG | AJM | FREEZER LIGHT NOT WORKING | AHSAN |  | 18:15 | 18:40 | NEED TO REPLACE THE LIGHTS, ONE LIGHT HO;DER DAMAGE | NEED: T8 58W LIGHT DAY LIGHT (150CM, 5FT)-9NOS, T8 36W WARM WHITE (120CM, 4FT)-2NOS, TUBE LIGHT HOLDER-1NO |  | ATTENDED | NEED MATERIAL
2026-01-05 | 8:29 | 120260100 | 120260049 | 3 | AMC | NESTO | AJF | AJM | WATER LEAK IN THE FREEZER | VIGNESH | SELVAN | 9:25 | 11:00 | FOUND INSULATION DAMAGE, NEED TO REPLACE | NEED: INSULATION /8" ID * 3/8 TK-5NOS, BLACK FOAM TAPE-7NOS |  | ATTENDED | NEED MATERIAL
2026-01-05 | 10:51 | 120260101 | 120260060 | 1 | AMC | NESTO | AJE | AJM | ISLAND FREEZER TEMP ISSUE | SELVAN |  | 11:30 | 13:00 | FREEZER IS WORKING NORMAL, ALL FREEZER WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-05 | 18:15 | 120260102 | 120260048 | 2 | AMC | NESTO | AJG | AJM | CHILLER LIGHT NOT WORKING | AHSAN |  | 18:50 | 19:30 | NEED TO REPLACE THE LIGHTS | NEED: T5 28W 55CM WHITE COLOUR-2NOS, T5 28W 29CM WHITE COLOUR-4NOS, T5 28W 115CM WHITE COLOUR-6NOS, LED LIGHT FULL SET 115CM-8NOS |  | ATTENDED | NEED MATERIAL
2026-01-05 | 9:08 | 120260103 | 120260061 | 1 | AMC | ANSAR | KARAMA | DXB | COLD ROOM LIGHT NOT WORKING | SARAVANAN |  | 13:00 | 13:15 | NEED TO REPLACE THE DAMAGED LIGHTS | NEED: 5FT LED LIGHT-1, 4FT NORMAL TUBE ROD-1SET |  | ATTENDED | NEED MATERIAL
2026-01-05 | 9:33 | 120260104 | 120260062 | 2 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | CHILLER NOT WORKING | MOHAMMED |  | 11:30 | 13:30 | FOUND COND FAN MOTOR, MAIN BREAKER AND OVERLOAD DEFECTIVE. NEED TO REPLACE | NEED: COND FAN MOTOR (S4E420-AUH03-08)-2, MCB BREAKER (C60HC)-1, OVERLOAD LRA32-1 |  | COMPLETED | WORK COMPLETED | ON 8JAN26
2026-01-05 | 10:12 | 120260105 | 120260063 | 1 | AMC | AL FALAJ | ABU HAIL | DXB | UIT ROOM AC NOT WORKING | SARAVANAN | MOHAMMED | 15:30 | 19:00 | FOUND OUT DOOR COND FAN MOTOR DEFECTIVE, FOR NOW TRANSFERRED THE FAN MOTHER FORM ANOTHER UNIT AND WORKING NROMAL. NEED TO REPAIR OR REPLACE THE FAN MOTOR |  |  | ATTENDED | NEED FOR REPAIR
2026-01-05 | 11:16 | 120260106 | 120260064 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER NOT WORKING | AHSAN |  | 13:00 | 13:35 | FIXED THE SENSOE CLIP PROPERLY AND NOW UNIT RUNNING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-05 | 10:30 | 120260107 | 120260034 | 2 | AMC | HOP | JEBAL ALI | DXB | COLD ROOM ICE FORMATION | SARAVANAN |  | 10:30 | 11:15 | FREEZER COLD ROOM DOOR FRAME HEATER DAMAGE NEED TO REPLACE | NEED: 142CM * 202CM-1SET DOOR FRAME HEATER |  | ATTENDED | NEED MATERIAL
2026-01-05 | 13:01 | 120260108 | 120260065 | 1 | AMC | LULU | DIP | DXB | LIGHT NOT WORKING | SADAM |  | 18:30 | 19:30 | NEED TO REPLACE THE LIGHT | NEED: 4FT T5 LED 24V-2NOS |  | ATTENDED | NEED MATERIAL
2026-01-05 | 15:03 | 120260109 | 120260066 | 1 | AMC | ANSAR | KARAMA | DXB | CHILLER WATER LEAK | RACEL | ROGER | 21:38 | 23:05 | REMOBVE THE CABINETCOVER AND FOUND WATER, STOCK ON CABINET. PUMP THE DRAINAGE LINK AND FLUSHING, CLEAN THE GARBAGE WATER AND NOW BLOCK FREE |  |  | COMPLETED | WORK COMPLETED
2026-01-05 | 15:00 | 120260110 | 1020250118 | 1 | AMC | LULU | DHAID | SHJ | MILK CHILLER TRIPPING | AHSAN |  | 15:00 | 16:45 | REPLACED THE DRAIN HEATER AND WORKING NROMAL | USED: 500W HEATER-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-05 | 17:52 | 120260111 | 120260067 | 1 | WTY | CAREEM | CITYLAND | DXB | COLD ROOM WATER PIMP MOISTURE ISSUE | SADAM |  | 20:00 | 9:30 | WE CLEAN AND ADD HEATER TO DRAIN PUMP IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-05 | 20:55 | 120260112 | 120260068 | 1 | AMC | CAREEM | MARINA 1 | DXB | CHEST FREEZER NOT WORKING | SADAM |  | 22:00 | 1:00 | REPAIR THE FELECTRICAL WIRE AND TURN ON THE FREEZER RUNNING BACK TO NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-05 | 22:00 | 120260113 | 920250547 | 1 | AMC | AL FALAJ | ABU HAIL | DXB | BLOWER INSTALLATION | ABID, AJMEER | SHAHABUDDIN, RANJITH |  |  | REPLACE NEW BLOWER MOTOR FIX THE BLOWER MOTOR IN FCU AND NEED TO REPLACE THE CONDENSER FAN MOTOR ALSO | USED: BLOWER FAN MOTOR-1, NEED: COND FAN MOTOR-1 |  | ATTENDED | NEED MATERIAL
2026-01-05 | 10:21 | 120260114 | 120260069 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | STORE FREEZER TEMP IS NOT WORKING IN BAKERY SECTION | FROILAN | OLIVER | 11:20 | 13:55 | REMOVING THE ICE FORMATION IN EVP COIL AND ADJUST THE SETTING AT DEFROSTING / COMBI FREEZER F#7 COOL DOWN THE COMPRESOR AND START THE UNIT, UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-05 | 10:24 | 120260115 | 120260070 | 2 | AMC | AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER AND VEG FREEZER / BUTCHERY DISPLAY CHILLER HIGH TEMP | FROILAN, OLIVER | WILLIAM | 15:03 | 16:30 | REMOVE THE UNIT BELOW THE CABINET DRAIN PIPE DECLOGGED AND CLEAN THE FAN GRILL AT BUTCHERY / FOUND FAN MOTOR DEFECTIVE | NEED: 16-30W FAN MOTOR-1 |  | COMPLETED | WORK COMPLETED | ON 13JAN26
2026-01-05 | 10:47 | 120260116 | 120260071 | 1 | AMC | AD COOP/DEYAAR | ZAYEST 1ST | AUH | ICE FORMING IN THE STORAGE FREEZER | FROILAN, OLIVER | WILLIAM | 17:02 | 17:45 | REPAIRED THE DRAIN PIPE AND REMOVED THE ICE FORMATION, FRAME HEATER FOUND DEFECTIVE AND DOOR GASKET DAMAGE | NEEd: FRAME HEATER WIRE TYPE 4MM*6MTRS 220V-1, DOOR GASKET 6MTRS-1, SILICON SEALNT-2, ALUMINUM ANGLE BAR 2*2-1MTR, SELF SCREW 1"-20NOS |  | ATTENDED | NEED MATERIAL
2026-01-05 | 11:21 | 120260117 | 120260072 | 3 | AMC | AD COOP/DEYAAR | MBZ | AUH | ICE FORMATION IN THE INSULATION | RANDOLPH | TROVEE |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 6JAN26
2026-01-05 | 11:42 | 120260118 | 120260073 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | INSTALLATION OF ICE MACHINE / ICE CREAM FREEZER IS NOT WORKING | RANDOLPH | TROVEE | 14:20 | 17:10 | INSTALLED THE USED ICE MACHINE AND DISMANTLED THE DEFECTIVE / ADDITIONAL TEMP SET POINT FOR ICE CREAM FREEZER | NEED: R404A-5CYLS |  | ATTENDED | NEED MATERIAL
2026-01-05 | 19:04 | 120260119 | 120260074 | 2 | AMC | AD COOP/DEYAAR | SPAR SAADIYAT | AUH | CHEESE CHILLER NOT WORKING | RANDOLPH | TROVEE | 20:50 | 21:30 | UNDERCHARGE OF REF AND NEED TO CHARGE, GAS LEAK FOUND IN PIN VALVE | NEED: R404A-1CYL |  | ATTENDED | NEED MATERIAL
2026-01-05 | 22:43 | 120260120 | 120260075 | 2 | AMC | AD COOP/DEYAAR | MINA | AUH | ICE MACHINE NOT WORKING | FROILAN | WILLIAM |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 6JAN26
2026-01-05 | 9:11 | 120260121 | 120260076 | 1 | AMC | TCS | FALCON KHALIDIYA | AUH | F&V CHILLER HIGH TEMP | FROILAN, OLIVER | WILLIAM | 10:10 | 12:53 | CHARGED REF DUE TO LOW REF. LEAK AT LIQUID LINE ABOVE SETTING AND REPAIRED | USED: R404A-1CYL BY STORE |  | COMPLETED | WORK COMPLETED
2026-01-05 | 9:27 | 120260122 | 120260077 | 1 | AMC | TCS | JVC MANHATTAN | DXB | FREEZER WATER LEAK | SHAFI | MUSTAFA | [5 empty] | COMPLETED
2026-01-05 | 10:21 | 120260123 | 7100289375 | 1 | AMC | ENOC | 1054 | DXB | ICE FORMATION IN WALKIN FREEZER | RACEL | ROGER | 24:09 | 2:15 | REMOVE THE DOOR AND CHECK, REOMVED ICE AND DOOR LOCK HANDLE ADJUSTED. SILICONED THE SCREW, WATER DROP DURING DEFROST/. ALIGNESD THE FLOOR LEVEL AND DOOR CLOSED PROPERLY |  |  | COMPLETED | WORK COMPLETED
2026-01-05 | 10:21 | 120260124 | 7100289376 | 1 | AMC | ENOC | 1054 | DXB | ICE FORMATION IN WALKIN FREEZER | RACEL | ROGER | 24:09 | 2:15 | REMOVE THE DOOR AND CHECK, REOMVED ICE AND DOOR LOCK HANDLE ADJUSTED. SILICONED THE SCREW, WATER DROP DURING DEFROST/. ALIGNESD THE FLOOR LEVEL AND DOOR CLOSED PROPERLY |  |  | COMPLETED | WORK COMPLETED
2026-01-05 | 10:21 | 120260125 | 7100289394 | 2 | AMC | ENOC | 1027 | DXB | WALKIN CHILLER DOOR TOUCHING | SHAFI, DENNIS | MUSTAFA |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 6JAN26
2026-01-05 | 10:21 | 120260126 | 7100289467 | 1 | AMC | ENOC | 1205 | AJM | BACKUP FREEZER HAVE ICE FORMATION | RACEL | ROGER | 19:52 | 20:40 | UNIT NOT OUR SCOPE |  |  | ATTENDED | NOT UNDER OUR SCOPE
2026-01-05 | 12:38 | 120260127 | 7100289285 | 1 | AMC | ENOC | 1606 | DXB | DISPLAY CHILLER DOOR NEED TO FIX | [7 empty] | NOT ATTENDED | NOT UNDER OUR SCOPE
2026-01-05 | 18:30 | 120260128 |  | 0 | AMC | ENOC | 401 | RAK | CHILLER CABINET DOOR NOT CLOSING AND GASKET DAMAGE | SABITH ALI |  | 18:30 | 19:10 | FIT IN THE GASKET AND CABINET DOOR ALSO DAMAGE |  |  | COMPLETED | WORK COMPLETED
2026-01-05 | 14:40 | 120260129 | 7100289100 | 2 | AMC | ENOC | 508 | FUJ | OPEN CHILLER TRIPPING ISSUE | VIGNESH | SELVAN | 14:40 | 19:00 | REPLACED THE COMPRESSOR, FILTER DRIER AND REPROCESS DONE | USED: COMPRESSOR (NJ9238GK)-1, R404A-1, FILTER DRIER 1/2 SOLDER-1, BRAZING ROD-2NOS, FAN MOTOR |  | COMPLETED | WORK COMPLETED
2026-01-05 | 19:30 | 120260130 | 7100284959 | 1 | AMC | ENOC | 412 | RAK | VERTICAL CHILLER BOTTOM COVER AND CABINET SHELF REPAINTING | SABITH ALI |  | 19:30 | 19:55 | INSPECTED THE VERTICAL CHILLER AND NEED TO REPAINT THE BOTTOM COVERS AND CABINET SHELVES |  |  | ATTENDED | NEED MATERIAL
2026-01-05 | 8:00 | 120260131 |  | 0 | AMC | ENOC | 509 | FUJ | WALKIN CHILLER AND FREEZER SHELVES REMOVE | BIJU, LORIMER | ABIJITH, SUDHEESH, WILSON | 8:45 | 11:30 | PULLOUT ALL SHELVES FROM THE FREEZER AND CHILLER AND GIVEN FOR COATING |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 9:24 | 120260132 |  | 0 | AMC | ENOC | 1205 | AJM | CHILLER GOING ON -VE TEMP | VIGNESH | SELVAN | 9:45 | 12:15 | DEFECTIVE CONTROLLER REPLACED AND UNIT WORKING NORMAL | USED: EDANFOSS EKC 202D-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-06 | 16:14 | 120260133 | 7100289710 | 2 | AMC | ENOC | 1052 | DXB | GASKET FOR WALKIN FREEZER DOOR, DAMAGE | SHAFI | MUSTAFA |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 14JAN26
2026-01-06 | 16:14 | 120260134 | 7100289763 | 2 | AMC | ENOC | 1035 | DXB | DRAIN PIPE LINE IN WALKIN CHILLER | SABITH ALI |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 8JAN26
2026-01-06 | 16:14 | 120260135 | 7100289801 | 2 | AMC | ENOC | 1085 | DXB | VERTICAL FREEZER NEED TO CHECK | SADAM |  | 24:00 | 2:00 | FOUND DEFROST HEATER DEFECTIVE |  |  | COMPLETED | WORK COMPLETED | ON 8JAN26
2026-01-06 | 16:14 | 120260136 | 7100289807 | 3 | AMC | ENOC | 4002 | DXB | WATER LEAK FROM CHILLER#2 | SABITH ALI |  |  |  | ATTENEDED |  |  | ATTENDED | ATTENDED ON 7JAN26
2026-01-06 | 9:25 | 120260137 | 120260078 | 1 | AMC | LULU | MAQAM | AL AIN | FREEZER COLD ROOM HIGH TEMP | TALIB |  | 10:25 | 12:05 | CHECKED FREEZER COLD ROOM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 13:18 | 120260138 | 120260079 | 1 | AMC | LULU | AL KHARIR | AL AIN | MILK CHILLER HIGH TEMP | TALIB |  | 19:50 | 22:20 | PRIMARY COIL LEAK | NEED: 3/8 COPPER PIPE-1 ROLL, R600-1CYL, BLUE ROD-2, FILTER DRIER 1/4-1 |  | ATTENDED | NEED MATERIAL
2026-01-06 | 13:25 | 120260139 | 120260080 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | VEG CHILLER TRIPPING | SADAM |  | 19:30 | 20:55 | REPLACED THE NEW EVP FAN MOTOR AND UNIT RUNNING NORMAL | USED: 10W FAN MOTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-06 | 13:42 | 120260140 | 120260081 | 1 | AMC | ANSAR | KARAMA | DXB | COMBI FREEZER NOT COOLING | AHSAN |  | 16:00 | 17:00 | CHANGED DEFROST AND TEMP OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 13:51 | 120260141 | 120260082 | 2 | AMC | GOURMET | AL REEM | AUH | CHILLER HIGH TEMP | OLIVER | FROILAN, WILLIAM |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 7JAN26
2026-01-06 | 14:30 | 120260142 | 120260083 | 1 | AMC | LULU | JADHAF | DXB | BAKERY CHILLER COMMISSIONG | SARAVANAN |  | 16:00 | 17:45 | FIXED THE DOOR AND BOTTOM TRAY AND FIX SUPPLY GRILLS. CHECK THE WIRING AND VOLTAGE AND AMPS. WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 12:30 | 120260143 | 120260084 | 1 | AMC | WESTLAND | AL AIN | AL AIN | VISUAL CHECK | TALIB |  | 13:30 | 18:35 | REPAIR THE LEAK AND VACUUM THE SYSTEM AND REF CHARGED | USED: R404A-1 BY STORE |  | COMPLETED | WORK COMPLETED
2026-01-06 | 19:42 | 120260144 | 120260085 | 1 | AMC | LULU | NUAIMIA | AJM | HOT FOOD CHILLER GETTING TOO MUCH COLD | RACEL |  | 24:20 | 1:10 | FOUND DRAIN PAN HEATER DEFECTIVE, NEED TO REPLACE | NEED: DRAIN PAN HEATER 33CM, 220V-1NO |  | ATTENDED | NEED MATERIAL
2026-01-06 | 8:51 | 120260145 | 120260086 | 2 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE NOT WORKING | FROILAN | WILLIAM | 10:52 | 11:30 | WATER INLET VALVE NOT WORKING STUCK IUP | NEED: SINGLE WTAER INLET VALVE 220VAC-1NO |  | COMPLETED | WORK COMPLETED | ON 6JAN26
2026-01-06 | 8:35 | 120260146 | 120260075 | 2 | AMC | AD COOP/DEYAAR | MINA | AUH | ICE MACHINE NOT WORKING | FROILAN | WILLIAM | 8:35 | 9:20 | CLEANED THE CONDENSER COIL, REMOVED AND ICE |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 9:47 | 120260147 | 120260087 | 2 | AMC | AD COOP/DEYAAR | MUROOR | AUH | CHEESE STORAGE CHILLER NOT WORKING | RANDOLPH | TROVEE | 11:24 | 12:07 | COMPRESSOR FOUND DEFECTIVE | NEED: COMPRESSOR-1, FILTER DRIER 3/8 FLARE-1, NITROGEN R16-1, R141B-1CYL, R22-1CYL, EVP UNIT DUAL FAN-1NOS |  | ATTENDED | NEED MATERIAL
2026-01-06 | 10:19 | 120260148 | 120260088 | 1 | AMC | AD COOP/DEYAAR | MADINAT ZAYED | AUH | COLD ROOM ICE FORMATION | FROILAN | WILLIAM | 15:50 | 16:30 | FOUND COLD ROOM ICE FORMATION, DUE TO AIR LAKEAGE GAPS | NEEd: INSULATION FOAM TAPE BLACK COLOUR 2"-1 ROLL, PVC CURTAIN PLAIN 300CM-2NOS |  | COMPLETED | WORK COMPLETED
2026-01-06 | 11:28 | 120260149 | 120260089 | 1 | AMC | AD COOP/DEYAAR | HAMDAN | AUH | BUTCHERY COLD STORAGE ICE FORMATION / CHILLER WTAER LEAK | RANDOLPH | OLIVER, TROVEE | 13:54 | 14:24 | REPAIR DRAIN AGE DRAIN PIPE, REMOVED THE ICE FORMATION AT COLD ROOM CURTAIN AND ADJUST THE COLD ROOM DOOR DUE TO AIR LEAK, SUBJECT TO REPLACE COLD ROOM GASKET |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 12:40 | 120260150 | 120260072 | 3 | AMC | AD COOP/DEYAAR | MBZ | AUH | ICE FORMATION IN THE INSULATION | RANDOLPH | TROVEE | 12:40 | 1:00 | INSULATION DAMAGE | NEED: INSULATION 54MM*25MM-5NOS, INSULATION TAPE 2"-3NOS |  | COMPLETED | WORK COMPLETED
2026-01-06 | 16:01 | 120260151 | 120260090 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | F7 FREEZER HIGH TEMP | RANDOLPH | OLIVER, TROVEE | 17:08 | 17:25 | COMPRESSOR OVERHEAT DUE TO THAT HIGH TEMP ALARM, DUE TO AMBIENT NEED TO SWITCH ON THE FCU UNIT |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 16:47 | 120260152 | 120260091 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | ICE CREAM FREEZER NOT COOLING | RANDOLPH | OLIVER, TROVEE | 17:48 | 18:35 | TRIP OFF OIL PRESSURE SWITCH AND RESTART THE UNIT |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 17:48 | 120260153 | 120260086 | 2 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE NOT WORKING | RANDOLPH | OLIVER, TROVEE | 17:48 | 18:35 | REPLACED THE ETARE SOLENOID VALVE AND RESTART THE UNIT WORKING NORMAL | USED: SINGLE WTAER INLET VALVE 220VAC-1NO |  | COMPLETED | WORK COMPLETED
2026-01-06 | 20:26 | 120260154 | 120260092 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | VEG CHILLER STORE WATER LEAK | OLIVER | FROILAN, WILLIAM |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 7JAN26
2026-01-06 | 11:03 | 120260155 | 120260093 | 1 | AMC | TCS | GREENS | DXB | STEEL BODY CHILLER HIGH TEMP / CHILLER WATER LEAK | SHAFI | MUSTAFA |  |  | PERMIT ISSUE |  |  | ATTENDED | NEED PERMIT
2026-01-06 | 13:34 | 120260156 | 120260094 | 1 | AMC | TCS | JVC MANHATTAN | DXB | BSEMENT PARKING AREA NOISE ISSUE | SHAFI | MUSTAFA | 14:10 | 15:15 | BEARING AREA GREESE AND OILED, NEED TO FIX DOX FAN MOTOR FOR THE FREEZER CABINET | NEED: BOX FAN MOTOR 120*120-5NOS, CABLE 1.5MM*3C-3MTR, BLOWER BELT A55-6NOS |  | ATTENDED | NEED MATERIAL
2026-01-06 | 10:25 | 120260157 | 120260095 | 1 | AMC | NESTO | AJF | AJM | BACK STORE CHILLER EVP ICE FORMATION | VIGNESH | SELVAN | 12:55 | 13:25 | CONTROLLER DEFECTIVE, NEED TO REPLACE | NEED: AKO CONTROLLER-1, CONTCATOR LC1D12-1NO |  | ATTENDED | NEED MATERIAL
2026-01-06 | 10:26 | 120260158 | 120260096 | 2 | AMC | NESTO | AJJ | AJM | BUTCHERY CHILLER HIGH TEMP | VIGNESH | SELVAN | 14:00 | 16:15 | FIX THE WIRE PROBLEM AND REPIARED UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 13:12 | 120260159 | 120260097 | 1 | AMC | NESTO | SATWA | DXB | DELI CHILLER WTAER LEAK / ALL COLD ROOM DOOR HANDLE CHECK | SADAM |  | 21:20 | 23:30 | DELI CHILLER SUCTION PIPE SIDE PUT SILICON AND MANUALLY PULLE THE WATER / DOOR HANDLE RECTIFY AND FOUND SAFETY LOCK DAMAGE | NEED: DOOR HANDLE SAFETY LOCK-6SET |  | ATTENDED | NEED MATERIAL
2026-01-06 | 15:12 | 120260160 | 120260098 | 1 | AMC | NESTO | FUJAIRAH MALL | FUJ | BAKERY CHILLER HIGH TEMP | SABITH ALI |  | 18:40 | 19:15 | GLASS MISSING AND DUE TO RETURN AIR THE TEMP GETTING HIGH, NEED TO INSTALL THE GLASS | NEED: ACRYLIC SHEET-1 (LENGTH-250CM, HEIGHT-25CM) |  | ATTENDED | NEED MATERIAL
2026-01-06 | 19:11 | 120260161 | 120260096 | 2 | AMC | NESTO | AJJ | AJM | BUTCHERY CHILLER HIGH TEMP | RACEL | ROGER | 19:11 | 23:50 | DEFECTIVE CONTROLLER REPLACED AND UNIT WORKING NORMAL | USED: EKC 202D DANFOSS CONTROLLER-1, NTC SENSOR-2NOS |  | COMPLETED | WORK COMPLETED | REPEAT COMPLAINT
2026-01-06 | 23:00 | 120260162 | 120260100 | 1 | AMC | NESTO | KARAMA | DXB | PARKING AREA INSULATION REPLACEMENT | ROGER | GOVIND, ZALAUDDIN | 23:30 | 8:00 | REPLACED THE INSULATION AND NEED TO MAKE TAPE IN THE PIPE LINE |  |  | COMPLETED | WORK COMPLETED
2026-01-06 | 9:00 | 120260163 | 7100289394 | 2 | AMC | ENOC | 1027 | DXB | WALKIN CHILLER DOOR TOUCHING | SHAFI, DENNIS | MUSTAFA | 9:45 | 12:00 | TEMPORARY REPAIRED AND ALIGN THE BOTTOM HINGES | NEED TO REPLACE FULL FRAME AND DOORS FREEZER DOOR PANEL |  | COMPLETED | WORK COMPLETED
2026-01-06 | 13:38 | 120260164 |  | 0 | AMC | ENOC | 509 | FUJ | PAINTING OF CHILELR AND FREEZER SUPPORT AND FRAME | SABITH ALI | BIJU, LORIMER | 15:30 | 22:00 | ALL SUPPORT AND FRAME PAINTING FOR FREEZER AND CHILLER DONE | REMIANING PANEL CLEANING AND RETURNING THE CHAKKER PLATE |  | COMPLETED | WORK COMPLETED
2026-01-06 | 14:17 | 120260165 |  | 0 | AMC | ENOC | 1045 | RAK | VERTICAL GFREEZER TRIPPING | SHAFI | MUSTAFA | 16:15 | 19:30 | FOUND DRAIN HEATER DEFECTIVE AND REPLACED UNIT WORKING NORMAL | USED: DRAIN HEATER-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-06 | 14:26 | 120260166 | 7100277058 | 1 | AMC | ENOC | 1179 | SHJ | REPLACEMNET OF LED LIGHT FOR FREEZER | VIGNESH | SELVAN | 17:10 | 19:00 | FIX THE NEW LED LIGHT AND WORKING NROMAL | USED: MODI LED FULL SET LIGHT-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-06 | 10:08 | 120260167 | 120260101 | 2 | AMC | ADNOC | 596 | FUJ | FREEZER NOISE ISSUE | SABITH ALI |  | 16:30 | 18:15 | REMOVED THE ICE FORMATION BY MANUAL DEFROST AND CHECKED AND ADJUSTED DEFROST SETTING | FOR NOW NOT POSSIBLE TO CHECK, DUE TO WOOD BLOCK AND PANEL NEED TO REMOVED TO CHECK |  | COMPLETED | WORK COMPLETED
2026-01-06 | 17:57 | 120260168 | 120260102 | 3 | AMC | ADNOC | 634 | SHJ | ICE MACHINE WATER LEAK | SABITH ALI |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 7JAN26
2026-01-06 |  | 120260169 | PPM | 37 | AMC | HOP | JEBAL ALI | DXB | PPM | SUDHEESH | ABIJITH |  |  | ALL UNIT OUT DOOR AND INDOOR FILTER SERVICE DONE |  |  | COMPLETED | WORK COMPLETED
2026-01-06 |  | 120260170 | PPM | 37 | AMC | CAREEM | MOTOR CITY | DXB | PPM | ABID, AJMEER | RANJITH, SHAHABUDDIN |  |  | ALL UNIT CHECKED AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-06 |  | 120260171 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 6:15 | 19:10 | SHARJAH ACCOMADATION PICK UP AND DROP IN HOP, ABU DHABI MATERIAL DELIVERY |  |  | COMPLETED | WORK COMPLETED
2026-01-07 | 9:13 | 120260172 | 120260103 | 1 | AMC | CAREEM | JVC PLAZA | DXB | CHILLER SLIDING DOOR ISSUE | MOHAMMED |  | 10:00 | 11:00 | REMOVE THE DOOR AND MAKE THE TIGHTEN AND CLEAN THE WHEEL AND SUPPORT REFIX, NEED DOOR WHEEL AND SUPPORT | NEED: DOOR WHEEL-4NOS, DOOR CLOSE SPRING-2NOS |  | ATTENDED | NEED MATERIAL
2026-01-07 | 9:16 | 120260173 | 120260104 | 2 | AMC | EVERMORE | DIP | DXB | WATER LEAK FROM THE INSULATION | MOHAMMED |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 8JAN26
2026-01-07 | 10:35 | 120260174 | 120260105 | 1 | WTY | CAREEM | DIERA | DXB | FREEZER COLD ROOM HIGH TEMP | SHAFI | MUSTAFA | 16:10 | 17:45 | RELOCATED THE SENSOR AND UNIT WORKING NROMAL AND TEMP IS OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-07 | 10:46 | 120260175 | 120260106 | 2 | AMC | CAREEM | JLT | DXB | CHEST FREEZER NOT WORKING / FREEZER NO#6 HIGH TEMP ISSUE | MOHAMMED |  | 12:00 | 14:00 | CHEST FREEZER NEED TO REPLACE TOP DOOR / FREEZER HAVE LEAK AND WORKING IN VACUUM STAGE, NEED TO PULL OUT THE CABINET AND CHECK | NEED: CHEST FREEZER DOOR-1 (EV100ICF) 29*43CM | Freezer cabinet work done(22/1/2026) | ATTENDED | NEED MATERIAL
2026-01-07 | 11:05 | 120260176 | 120260082 | 2 | AMC | GOURMET | AL REEM | AUH | CHILLER HIGH TEMP | OLIVER | FROILAN, WILLIAM | 11:05 | 11:48 | CHARGHED THE ADDITIONAL REF AND NO FOUND ANY LEAK | USED: R404A BY STORE |  | COMPLETED | WORK COMPLETED
2026-01-07 | 4:27 | 120260177 | 5000215126 | 1 | AMC | ENOC | 1205 | AJM | OPEN CHILLER CONTINOUSLY IN DEF MODE | AHSAN |  | 9:30 | 10:40 | CHANGED DEFROST INTERVAL EVERY 6 HOURS AND REDUSE THE DEFROST TEMP +12 |  |  | COMPLETED | WORK COMPLETED | REPEAT COMPLAINT
2026-01-07 | 10:58 | 120260178 | 5000203210 | 1 | AMC | ENOC | 1401 | RAK | SKOPE VERTICAL CHILLER UNIT NEED TO CHACK AND CONDITION REPORT | VIGNESH | SELVAN | 14:00 | 14:35 | FOUND GASKET ISSUE IN 4 DOORS, RUST AND DAMAGE, COOLING EFFICIENCY IS NORMAL. BETTER REPLACE THE UNIT | NEED TO REPLACE THE UNIT |  | COMPLETED | WORK COMPLETED
2026-01-07 | 12:42 | 120260179 | 7100288245 | 2 | AMC | ENOC | 1092 | DXB | PVC CURTAIN REPLACEMENT | MOHAMMED |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 8JAN26
2026-01-07 | 10:58 | 120260180 | 5000210566 | 1 | AMC | ENOC | 401 | RAK | GASKET ISSUE | VIGNESH | SELVAN | 12:00 | 13:00 | REFIXED THE GASKET TEMPORARY IN THE UNIT, NEED TO REPLACE THE GASKET |  |  | COMPLETED | WORK COMPLETED
2026-01-07 | 12:46 | 120260181 | 7100289896 | 2 | AMC | ENOC | 305 | UMQ | CHILLER DOOR NOT CLOSING PROPERLY | AHSAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 9JAN26
2026-01-07 | 12:46 | 120260182 | 7100289958 | 2 | AMC | ENOC | 1088 | DXB | WALKIN FREEZER DOOR GASKET | SHAFI | MUSTAFA |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 8JAN26
2026-01-07 | 12:46 | 120260183 | 7100290004 | 1 | AMC | ENOC | 1042 | DXB | WALKIN FREEZER | MOHAMMED |  | 16:00 | 17:00 | SYSTEM UNDERCHARGE AND FOUND NO LEAK AND CHARGED REF, IF AGAIN SAME ISSUE NEED TO DO LEAK TEST |  |  | COMPLETED | WORK COMPLETED
2026-01-07 | 13:06 | 120260184 | 120260102 | 3 | AMC | ADNOC | 634 | SHJ | ICE MACHINE WATER LEAK | SABITH ALI |  | 14:00 | 14:45 | WATER FILTER SET NEED TO REPLACE | NEED: WATER FILTER SET-1 |  | COMPLETED | WORK COMPLETED | ON 16JAN26
2026-01-07 | 14:00 | 120260185 | 7100289807 | 3 | AMC | ENOC | ZOOM4002 | DXB | WATER LEAK FROM CHILLER#3 | SABITH ALI |  | 15:45 | 17:00 | CHECKED THE DRAIN PAN HEATER, FLOAT SWITCH IS DAMAGE. NEED TO REPLACE | NEED: DRAIN PAN HEATER 75CM-1, DRAIN PAN FLOAT SWITCH-1, MAG CONTACTOR 12AMPS-1 |  | COMPLETED | WORK COMPLETED | ON 17JAN26
2026-01-07 | 8:45 | 120260186 | 120260107 | 1 | AMC | NESTO | KARAMA | AJM | COMBI FREEZER TRIPPING ISSUE / FREEZER COLD ROOM LIGHT NOT WORKING | SHAFI | MUSTAFA | 9:45 | 15:00 | FAN MOTOR FOUND DEFECTIVE AND REPLACED, MINUS RANGE RELAY RESETTED, PCB BOARD RESTARTED / REPLACED THE DEFECTIVE LIGHT AND WORKING NORMAL | USED: FAN MOTOR 10W-2 BY TD, LED LIGHT 4FT-2NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-07 | 10:48 | 120260187 | 120260108 | 3 | AMC | NESTO | AJC | AJM | FREEZER HIGH TEMP | AHSAN |  | 12:00 | 19:30 | CLEAN THE CONDENSER COIL AND CHARGED R22 AND CHANGED THE POITION OF THE FAN MOTOR | USED: R22-1.5CYLS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-07 | 14:32 | 120260188 | 120260109 | 2 | WTY | PASONS | 28 | FUJ | VEG CHILLER HIGH TEMP | VIGNESH | SELVAN | 16:20 | 18:10 | FOUND COMPRESSOR DEFECTIVE, NEED TO REPLACE | NEED: EMERSON COPELAND (CR53KQM-TFD-201)-1, FILTER DRIER 3/8 SOLDER-1, R22-1, BRAZING ROD-5NOS |  | COMPLETED | WORK COMPLETED | ON 8JAN26
2026-01-07 | 8:00 | 120260189 | 120260092 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | VEG CHILLER STORE WATER LEAK | OLIVER | FROILAN, WILLIAM | 9:06 | 10:26 | DRIN PIPE DETACHED AND REPAIRED |  |  | COMPLETED | WORK COMPLETED
2026-01-07 | 13:00 | 120260190 | 120260074 | 2 | AMC | AD COOP/DEYAAR | SPAR SAADIYAT | AUH | CHEESE CHILLER HIGH TEMP | RANDOLPH |  | 14:04 | 15:30 | REPAIR THE LEAK, VACUUM THE SYTEM AND CHARGED REF | USED: R404A-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-07 | 21:08 | 120260191 | 120260110 | 2 | AMC | BAQER MOHEBI | AL NADHA | DXB | TABLE TOP CHILELR DOOR ISSUE | AHSAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 8JAN26
2026-01-07 | 9:30 | 120260192 | 7100289487 | 1 | AMC | ENOC | 1205 | AJM | WALKIN FREEZER ICE FORMATION IN FLOOR | AHSAN |  | 9:30 | 10:40 | CHNAGED THE DEFROST CONTROLLER SETTING |  |  | COMPLETED | WORK COMPLETED
2026-01-07 | 18:20 | 120260193 | 7100289763 | 2 | AMC | ENOC | 1035 | DXB | DRAIN PIPE LINE IN WALKIN CHILLER | SABITH ALI |  | 18:20 | 19:30 | DRAIN PIPE CONNECTOR FITTED AND ADJUST PROPERLY AN D SECTION PIPE COIPPER INSULATION DAMAGE AND FILLED WELL INSULATION AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-07 | 9:00 | 120260194 |  | 0 | AMC | ENOC | 1019 | DXB | OPEN CHILLER NEED GLASS INSTALLATION | SADAM | MUTHUKUMAR | 9:00 | 12:30 | INSTALL NEW GLASS IN OPEN CHILLER#2 AND WORKING NORMAL | NEED: NEW GLASS (SIDE PANEL)-1NO |  | ATTENDED | NEED MATERIAL
2026-01-07 | 19:33 | 120260195 | 120260111 | 1 | AMC | TCS | DEC MARINA | DXB | DISPLAY FREEZER NOT WORKING | RACEL | ROGER | 21:13 | 24:00 | DEEP CLEAN THE EVP COIL AND HEATER FOUND DEFECTIVE | NEED: 360CM DEFROST HEATER 220V-1NO |  | ATTENDED | NEED MATERIAL
2026-01-07 | 17:59 | 120260196 | 120260112 | 1 | AMC | NESTO | WAREHOUSE | DXB | OUTSIDE COOLING BLOWER NOISE ISSUE | SABITH ALI |  | 19:45 | 20:35 | FOUND BLOWER MOTOR BELT BROKEN | NEED: BLOWER MOTOR BELT-3 (SPB 4100LA-4078LD) |  | ATTENDED | NEED MATERIAL
2026-01-07 | 24:05 | 120260197 | 120260108 | 3 | AMC | NESTO | AJC | AJM | ISLAND FREEZER LEAK RECTIFICATION | RACEL | ROGER | 24:50 | 4:20 | REMOVED THE ITEMS AND FOUND LEAK AND ARRESTED IN U BEND AREA OF EVP COIL, NEED COND FAN MOTOR | NEED: COND FAN MOTOR-2NOS |  | ATTENDED | NEED MATERIAL
2026-01-07 |  | 120260198 | PPM | 37 | AMC | CAREEM | DSO | DXB | PPM Q3 | GOVIND | ZALAUDDIN |  |  | FREEZER UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-07 |  | 120260199 | PPM | 37 | AMC | CAREEM | DWTC | DXB | PPM Q3 | GOVIND | ZALAUDDIN |  |  | CHILELR AND FREEZER UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-07 |  | 120260200 | PPM | 37 | AMC | CAREEM | AL SAFA | DXB | PPM Q3 | SUDHEESH | ABIJITH |  |  | ALL UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-07 |  | 120260201 | MONTHLY REPORT | 4 | AMC | AD COOP/DEYAAR | SPAR ZAKHER MALL | AL AIN | MONTHLY REPORT | TALIB |  |  |  | ALL CHILLER AND FREEZER UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-07 |  | 120260202 | PPM | 37 | AMC | BANAYA FORREST | BLUE WATER | DXB | PPM FOR KITCHEN HOOD | ABID, AJMEER | RANJITH, SHSHABUDDIN |  |  | CLENAED THE KITCHEN HOOD AND FILTER |  |  | COMPLETED | WORK COMPLETED
2026-01-07 |  | 120260203 | PPM | 37 | AMC | RNQ | AJMAN | AJM | PPM | BIJU | LORIMER |  |  | CLENAING OF CONDENSER UNITS |  |  | COMPLETED | WORK COMPLETED
2026-01-07 |  | 120260204 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 7:30 | 20:00 | TRANSPORT FOR PPM TEAM, MATERIAL DELIVER IN AJG AND AJC, SHJ ACCOMADATION, CAREEM MOTOR CIOTY, AL SAFA |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 9:42 | 120260205 | 7100290130 | 1 | AMC | ENOC | 1117 | SHJ | FREEZER TEMP ISSUE | SELVAN |  | 11:50 | 13:50 | REMOVE THE EVP COIL ICE AND REMOVED. CONTROLLER SETPOINT FIXED AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 12:49 | 120260206 | 7100290119 | 1 | AMC | ENOC | 404 | RAK | DRINKS CHILLER DOOR GASKET | [7 empty] | NOT ATTENDED | NOT UNDER OUR SCOPE
2026-01-08 | 12:49 | 120260207 | 7100290152 | 1 | AMC | ENOC | 1080 | DXB | WALKIN FREEZER ICE FORMATION AND RUSTY | SADAM | MUTHUKUMAR | 1:50 | 4:00 | CLEAN THE EVP ICE AND CHACKE THE DEFROST WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 12:49 | 120260208 | 7100290266 | 2 | AMC | ENOC | 1079 | DXB | PLASTIC CURTAIN IN WALKIN CHILLER | SADAM | MUTHUKUMAR |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 9JAN26
2026-01-08 | 8:42 | 120260209 | 120260110 | 2 | AMC | BAQER MOHEBI | AL NADHA | DXB | TABLE TOP CHILELR DOOR ISSUE | AHSAN |  | 10:30 | 11:30 | REMOVED DAMAGE SCREW IN THE TABLE TOP CHILLER DOOR AND FIXED NEW SCREWS |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 8:50 | 120260210 | 120260104 | 2 | AMC | EVERMORE | DIP | DXB | WATER LEAK FROM THE INSULATION | MOHAMMED |  | 10:00 | 12:45 | REMOVE THE DAMAGE SILICON AND CLEANED THE WATER AND APPLY THE SILICON AND DRY |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 9:29 | 120260211 | 120260113 | 1 | AMC | CAREEM | DIC | DXB | CONDENSATE PUMP WATER SWEATING ISSUE | MOHAMMED |  | 17:30 | 18:30 | REMOVE THE FILTER ARE CLENAED AND FILTER REFIXED AND APPLIED SILICON IS OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 10:35 | 120260212 | 120260114 | 1 | AMC | LULU | AL KHARIR | AL AIN | FISH CHILLER COLD ROOM DOOR HANDLE ISSUE | TALIB |  | 10:35 | 12:20 | REMOVED THE DAMAGE DOOR HANDLE SET AND REPLACED NEW | USED: DOOR HANDLE LOCK SET-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-08 | 15:07 | 120260213 | 120260053 | 2 | AMC | CAREEM | BANIYAS | DXB | WATER IN THE COLD ROOM PUMP | OLIVER | FROILAN, WILLIAM | 15:07 | 15:46 | REPLACED THE DEFECTIVE CONDENSATE WATER PUMP | USED: CONDENSATE PUMP (PC125A)-1NO |  | COMPLETED | WORK COMPLETED
2026-01-08 | 16:44 | 120260214 | 120260115 | 2 | PAYABLE | GRANDIOSE | AL SOYOUH | SHJ | COLD ROOM FREEZER NOT WORKING | RACEL | ROGER | 19:34 | 21:35 | NEED TO LEAK RECTIFICATION AND REPROCESS THE UNIT | NEED: R404A-1, NITROGEN SMALL-1, FILTER DRIER 3/8" SOLDER-1, NTC SENSOR-1 |  | ATTENDED | NEED MATERIAL
2026-01-08 | 21:44 | 120260215 | 120260116 | 1 | AMC | LULU | NUAIMIA | DXB | HOT FOOD CHILLER UNIT TOO MUCH COLD | RACEL | ROGER | 22:35 | 23:40 | FOUND NEED TO REPLACE MAG CONTACTOR AND RELAY WITH DRAIN PAN HEATER | NEED: RELAY SLA-12VDC-SL-A (30A) MAG CONTACTOR, 1PH, 220V, 25AMPS-1, 5CORE CBALE WIRE-1MTR, DRIAN PAN HETER 33CM 220V |  | ATTENDED | NEED MATERIAL | REPEAT COMPLAINT
2026-01-08 | 19:15 | 120260216 | 120260062 | 2 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | REPLACEMENT OF CONDENSER FAN MOTOR | SABITH ALI |  | 19:15 | 21:55 | REPLACVED THE CONDENSER FAN MOTOR, OVERLOAD AND CHARGED GAS | USED: COND FAN MOTOR (S4E420-AUH03-08)-2, OVERLOAD LRA32-1, R22-3KG BY TD |  | COMPLETED | WORK COMPLETED
2026-01-08 | 18:30 | 120260217 | 120260109 | 2 | WTY | PASONS | 28 | FUJ | VEG CHILLER HIGH TEMP | VIGNESH | SELVAN | 18:30 | 2:10 | REPLACED COMPRESSOR, FILTER DRIER AND REPROCESS DONE AND UNIT WORKING NROMAL | USED: EMERSON COPELAND (CR53KQM-TFD-201)-1, FILTER DRIER 3/8 SOLDER-1, R22-1, BRAZING ROD-5NOS, ELBOW 7/8-3, 7/8 PIPE-1MTR, HP LP HOSE-EACH1PC |  | COMPLETED | WORK COMPLETED
2026-01-08 | 14:00 | 120260218 | 7100288245 | 2 | AMC | ENOC | 1092 | DXB | PVC CURTAIN REPLACEMENT | MOHAMMED |  | 14:00 | 14:45 | REPLACED THE PLASTIC CURTAIN | USED: PLASTIC CURTAIN 198CM-3NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-08 | 9:30 | 120260219 | 7100289801 | 2 | AMC | ENOC | 1085 | DXB | VERTICAL FREEZER NEED TO CHECK | SHAFI | MUSTAFA | 9:30 | 15:00 | REMOVED THE COMPLETED UNIT IVCE FORMATION AND FOUND DRAIN HEATER DEFACTIVE AND REPLACED | USED: DRAIN HEATER-2NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-08 | 16:00 | 120260220 | 7100289958 | 2 | AMC | ENOC | 1088 | DXB | WALKIN FREEZER DOOR GASKET | SHAFI | MUSTAFA | 16:00 | 16:40 | FIX THE GASKET BY PUT NEW GLUE AND OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 13:38 | 120260221 |  | 0 | AMC | ENOC | 509 | FUJ | REFIXING OF SHELVES | BIJU | LORIMER, RAMZAN | 23:00 |  | REFIXED THE SHELVES FOR THE WALKIN FREEZER AND CHILLER AND SUPPORT REPAINTED |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 10:58 | 120260222 | 120260117 | 1 | AMC | TCS | SHOROOQ | DXB | BAKERY FREEZER COLD ROOM NOT WORKING | AHSAN |  | 12:40 | 17:00 | REMOVED THE EVP ICE AND CHANGED THE EVP SENSOR AND CHANGED THE DEFROST SETTING | USED: NTC SENSOR-1NO BY TD (CAR STOCK) |  | COMPLETED | WORK COMPLETED
2026-01-08 | 12:11 | 120260223 | 120260118 | 1 | AMC | TCS | UMS | DXB | FREEZER COLD ROOM AND FREEZER CABINET HIGH TEMP ISSUE / OPEN CHILLER NOT WORKING | SARAVANAN |  | 13:30 | 16:45 | ICE CREAM FREEZER MANUAL DEFROST DONE AND / FREEZER#2 EVP FAN MOTOR FOUND DEFECTIVE / FREEZER COLD ROOM REPLACED DEFECTIVE CONTACTOR AND WORKING NROMAL | USED: LC1D32M7 CONTACTOR-1NO BY TD / NEED: EBMPAPST (W1G200-EC87-20)-1 |  | ATTENDED | NEED MATERIAL
2026-01-08 | 14:08 | 120260224 | 120260119 | 1 | AMC | TCS | EMERALD COURT | DXB | PORK FREEZER WATER LEAK | SADAM | MUTHUKUMAR | 19:00 | 20:00 | REPAIR THE DRAIN PIPE AND CHECK MANUALLY THE LEAK |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 10:00 | 120260225 | 120260120 | 1 | AMC | TCS | JULPHAR TOWER | RAK | DISPLAY FREEZER#5 ICE CREAM INSUFFICIENT COOLING | DENNIS |  | 10:00 | 18:15 | FIXED THE ELECTRICAL CONNECTION CONTROLLER RETURN TO ORIGINAL CONNECTION, REPLACED THE DEFECTIVE EVP SENSOR OF FREEZER CABINET AND MANUAL DEFROST | USED: ECKELMANN SENSOR-1 FROM STORE |  | COMPLETED | WORK COMPLETED
2026-01-08 | 8:49 | 120260226 | 120260121 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | VEG CHILLER WATER LEAK | OLIVER | FROILAN, WILLIAM | 9:50 | 11:25 | DECLOGGED THE DRAIN LINE AND WATER FLOW OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 10:48 | 120260227 | 120260122 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | FREEZER NOT WORKING / PROMOTION CHILLER WTER LEAK | OLIVER | FROILAN, WILLIAM | 9:50 | 11:25 | PROMOTION CHILLER ICE FORMATION REMOVED / COMBI FREEZER CLEANED THE CONDENSER COIL CLEANED |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 13:08 | 120260228 | 120260123 | 1 | AMC | AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | FREEZER TEMP ISSUE | SADAM | MUTHUKUMAR | 21:30 | 1:15 | CLEANED THE EVP ICE AND CHARGED THE REF DUE TO UNDERCHARGE | USED: R404A-2NOS BY STORE / NEED R404A-3CYLS |  | ATTENDED | NEED TO CHCEK LEAK
2026-01-08 | 13:22 | 120260229 | 120260124 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | BUTCHERY CHILLER NOT COOLING | RANDOLPH | TROVEE | 13:35 | 14:52 | SWITCH ON THE CONTACTRO AND RESTART THE CONTROLLER OF BUTCHERY AND RETIGHT THE SUPPLY OF PRESSURE SWITCH AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 13:40 | 120260230 | 120260125 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | FISHERY STORAGE NOT WORKING | RANDOLPH | TROVEE | 15:00 | 15:10 | NEED TO REPLACE FAN MOTOR | NEED: 10-20W FAN MOTOR-1NO |  | COMPLETED | WORK COMPLETED | ON 8JAN26
2026-01-08 | 12:30 | 120260231 | 120260072 | 3 | AMC | AD COOP/DEYAAR | MBZ | AUH | ICE FORMATION IN THE INSULATION | OLIVER | FROILAN, WILLIAM | 12:30 | 14:35 | REPLACED THE INSULATION ON THE SUCTION PIPES OF FREEZER COMPRESSOR AND SWITCH ON THE UNIT | USED: INSULATIO-3NOS, 2" BLACK TAPE-1, INSULATION GLUE-1CAN BY TD |  | COMPLETED | WORK COMPLETED
2026-01-08 | 15:14 | 120260232 | 120260126 | 1 | AMC | AD COOP/DEYAAR | MINA | DXB | B31 UPRIGHT FREEZER SOUND COMING | RANDOLPH | TROVEE | 15:20 | 16:00 | ANTI CONDENSATION FAN MOTOR RELOCATED DUE TO VIBRATION AND NOISE |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 16:07 | 120260233 | 120260127 | 1 | AMC | AD COOP/DEYAAR | MINA | DXB | HEAVY DUST ACCUMULATION ON THE WALIN CHILELR GUARD | RANDOLPH | TROVEE | 16:00 | 16:40 | CLEANED THE FAN GUARD OF EVP FAN MOTOR |  |  | COMPLETED | WORK COMPLETED
2026-01-08 | 16:55 | 120260234 | 120260125 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | FISHERY STORAGE - FAN MOTOR REPLACEMENT | RANDOLPH | TROVEE | 16:55 | 17:20 | REPLACED THE FAN MTOOR AND RESTARTED THE UNIT WORKING NORMAL | USED: 10-20W FAN MOTOR-1NO BY ONTEGRA |  | COMPLETED | WORK COMPLETED
2026-01-08 | 19:31 | 120260235 | 120260128 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | CHEESE CHILLER HIGH TEMP | RANDOLPH | TROVEE | 21:55 | 23:00 | REPMACED THE FAN MTOOR AND CHARGED THE REF AND UNIT WORKING NORMAL | USED: R404A-5CYLS, FAN MOTOR10-20-1NO |  | COMPLETED | WORK COMPLETED
2026-01-08 | 9:25 | 120260236 | 120260129 | 1 | AMC | NESTO | KARAMA | DXB | BAKERY CHILLER TRIPPING ISSUE | SARAVANAN |  | 10:30 | 12:10 | LIGHT DAMAGE DUE WATER IN THE UNIT AND NEED TO REPLACE. CLEAN THE WATER AND DISCONNECTED THE LIGHT | NEED: 3FT WHITE LED SET 220V-3NOS |  | ATTENDED | NEED MATERIAL
2026-01-08 | 10:18 | 120260237 | 120260130 | 2 | AMC | NESTO | WAREHOUSE | DXB | COMPRESSOR AREA ICE FORMATIONA AND WATER LEAK | SADAM | MUTHUKUMAR |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 9JAN26
2026-01-08 | 1:59 | 120260238 | 120260049 | 3 | AMC | NESTO | AJF | AJM | RE-INSULATION OF FREEZER#1 | RACEL | ROGER | 1:59 | 6:35 | REMOCED OLD INSULATION AND INSTALL NE RUBBER INSULATION AND FREEZER#3 NEED TO INSULATION | NEED: RUBBER INSULATION 7/8*3/8 22MM*19MM-10NOS, BISON KIT-1CAN |  | ATTENDED | NEED MATERIAL
2026-01-08 |  | 120260239 | PPM | 37 | AMC | CAREEM | BB2 | DXB | PPM Q3 | GOVIND | ZALAUDDIN |  |  | ALL UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-08 |  | 120260240 | PPM | 37 | AMC | CAREEM | BB1 | DXB | PPM Q3 | ABID, AJMEER | RANJITH, SHAHABUDDIN |  |  | CLEANED ALL FREEZER AND CHILLER CONDENSER UNIT AND CHECKED ALL OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-08 |  | 120260241 | PPM | 37 | AMC | CAREEM | ARJAN | DXB | PPM Q3 | SUDHEESH | ABIJITH |  |  | UNIT ALL WORKING NROMAL, HAVE SOME UNITS DOOR ISSUE |  |  | COMPLETED | WORK COMPLETED
2026-01-08 |  | 120260242 | PPM | 37 | AMC | TCS | AL AWEER | DXB | PPM | SUDHEESH | ABIJITH |  |  | ALL UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-08 |  | 120260243 | DRIVING | 27 |  |  |  |  | DRIVING | WILLSON |  | 8:00 | 5:25 | TRANSPORT FOR TCS AL AWEER, MATERIAL COLLECTION IN QMAR AL HUDA, MATERIAL DELIVERY IN ABU DHABI |  |  | COMPLETED | WORK COMPLETED
2026-01-09 | 24:07 | 120260244 | 120260099 | 1 | AMC | TCS | FALCON KHALIDIYA | AUH | BAKERY CHILLER HIGH TEMP / FISH SECTION CHILLER | FROILAN |  | 9:58 | 11:15 | DISCONNECTED THE COMPEROSSOR TERMINAL IN RELAY / FISH CHILLER DISPLAY DIGITAL SOLAR SENSOR DAMAGE | NEED: CONDENSER FAN MOTOR 16-25W-1NO, DIGITAL SOLAR SENSOR-1 |  | ATTENDED | NEED MATERIAL
2026-01-09 | 7:33 | 120260245 | 120260131 | 1 | AMC | TCS | LAKES | DXB | CHILLER HIGH TEMP | SHAFI | MUSTAFA | [5 empty] | ATTENDED
2026-01-09 | 10:58 | 120260246 | 120260132 | 1 | AMC | TCS | SAFA PARK | DXB | DISPLAY FREEZER NOT WORKING | SHAFI | MUSTAFA | [5 empty] | COMPLETED
2026-01-09 | 12:40 | 120260247 | 120260133 | 1 | AMC | TCS | ROVE DOWNTOWN | DXB | FREEZER NOISE ISSUE | SHAFI | MUSTAFA | [5 empty] | ATTENDED
2026-01-09 | 8:56 | 120260248 | 120260134 | 1 | AMC | NESTO | FUJAIRAH MALL | FUJ | FREEZER NOISE ISSUE | RACEL | ROGER | [5 empty] | COMPLETED
2026-01-09 | 11:33 | 120260249 | 120260135 | 1 | AMC | NESTO | MUWAILHA | SHJ | DAIRY CHILELR WATER LEAK | AHSAN | [6 empty] | ATTENDED
2026-01-09 | 9:51 | 120260250 | 120260136 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | EGG CHILLER LIGHT NEED TO REPLACE / ISLAND FREEZER LIGHT NEED TO REPLACEMENT | SARAVANAN | [6 empty] | ATTENDED
2026-01-09 | 10:33 | 120260251 | 120260137 | 2 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | EGG & JUICE CHILLER TRIPPING ISSUE | SARAVANAN |  | 11:45 | 13:00 | TEMPORARY DIRECT THE TIME DELAY WIRE, NEED TO REPLACE | NEED: CEA CET 181-H 220V TIMER-1NO |  | COMPLETED | WORK COMPLETED
2026-01-09 | 11:33 | 120260252 | 120260138 | 1 | AMC | BAQER MOHEBI | ABU HAIL | DXB | VEG CHILLER HIGH TEMP | AHSAN |  | 15:40 | 17:20 | CHANGED THE NEW CONTACTOR AND INSULATE THE WIRE PROPERLY AND OKAY | NEED: CONTACTOR LC1D25M7-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-09 | 7:33 | 120260253 | 120260139 | 1 | AMC | AD COOP/DEYAAR | AD MALL | AUH | ICE MAKER NOT WORKING | OLIVER |  | 8:43 | 9:46 | POWER SUPPLY CONNECTOR DETACHED AND REPAIR THE CONNECTOR AND STARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-09 | 8:44 | 120260254 | 120260140 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER HIGH TEMP | OLIVER |  | 10:31 | 10:53 | UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-09 | 8:58 | 120260255 | 120260141 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | VEG STORAGE NOT WORKING / FISH COLD ROOM HIGH TEMP | OLIVER | FROILAN, WILLIAM | 11:30 | 12:50 | VEG CHILLER FAN MOTOR GROUNDED / FAN MOTOR DEFECTIVE AND FAN BLADE REMOVED AND PUT WATER IN THE PRIMARY COIL | NEED: ELCO FAN MOTOR 10-20W-1NO, ELCO FAN MOTOR 16-30W-1NO |  | COMPLETED | WORK COMPLETED | ON 9JAN26
2026-01-09 | 10:08 | 120260256 | 120260142 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | CHILLER WATER LEAK | RANDOLPH | TROVEE | 14:00 | 14:25 | FLUSHED THE DRAIN HOSE AND CHILLER WTAER LEAK DONE |  |  | COMPLETED | WORK COMPLETED
2026-01-09 | 10:10 | 120260257 | 120260143 | 2 | AMC | AD COOP/DEYAAR | MBZ | AUH | COMBI FREEZER NOT WORKING | OLIVER | FROILAN, WILLIAM | 13:40 | 14:10 | SOLENOID VALVE DEFECTIVE | NEED: CASTEL SOLENOID COIL HF2-1NO |  | COMPLETED | WORK COMPLETED | ON 9JAN26
2026-01-09 | 14:40 | 120260258 | 120260141 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | VEG STORAGE NOT WORKING / FISH COLD ROOM HIGH TEMP | OLIVER | FROILAN, WILLIAM | 14:40 | 15:45 | REPLACED THE BOTH UNIT FAN MOTOR AND RESTARTED THE UNIT WORKING NORMAL | USED: ELCO FAN MOTOR 10-20W-1NO, ELCO FAN MOTOR 16-30W-1NO |  | COMPLETED | WORK COMPLETED
2026-01-09 | 18:58 | 120260259 | 120260143 | 2 | AMC | AD COOP/DEYAAR | MBZ | AUH | COMBI FREEZER NOT WORKING | RANDOLPH | TROVEE | 19:40 | 20:00 | REPLACED THE DEFECTIVE SOLENOIS VALVE AND UNIT WORKING NORMAL | USED: CASTEL SOLENOID COIL HF2-1NO |  | COMPLETED | WORK COMPLETED
2026-01-09 | 20:12 | 120260260 | 1220250429 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | BAKERY COLD ROOM - REPLACEMENT OF FAN MOTOR AND REF CHARGING | RANDOLPH | TROVEE | 20:30 | 21:35 | CHARGED THE REF AND REPLACED THE DEFECTIVE FAN MOTOR | USED: R404A-7CYLS, FAN MOTOR 34W 220V-1 |  | COMPLETED | WORK COMPLETED
2026-01-09 | 22:13 | 120260261 | 120260144 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | FREEZER B38 NOT COOLING | RANDOLPH | TROVEE | 22:45 | 24:10 | DEFROST THE UNIT AND FOUND OUT MAG CONTACTOR OF DEFROST HEATER DEFECTIVE MANUALLY. REMOVED THE ICE FORMATION | NEED: MAG CONTACTOR-1, SILICON WHITE-2NOS |  | ATTENDED | NEED MATERIAL
2026-01-09 | 10:00 | 120260262 | 1220250409 | 1 | AMC | LULU | MAQAM | AL AIN | BACK STORE COLD ROOM TEMP ISSUE | TALIB |  | 12:05 | 13:45 | REMOVE THE OLD DOOR LIMIT SMITCH AND REPLACED NEW | USED: DOOR LIMIT SWITC-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-09 | 15:34 | 120260263 | 120260145 | 2 | AMC | LULU | SAADIYAT | AUH | FISH COLD ROOM HIGH TEMP ISSUE | RANDOLPH | TROVEE | 16:12 | 17:15 | FOUND COMPRESSOR DEFECTIVE, NEED TO REPLACE | NEED: COMPRESSOR EMBRACO (NJ9232GS)-1, R404A-1, FILTER DRIER SOLDER 3/8"-1, COND FAN MOTOR-1 |  | COMPLETED | WORK COMPLETED | ON 10JAN26
2026-01-09 | 15:15 | 120260264 | 120260137 | 2 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | EGG & JUICE CHILLER TRIPPING ISSUE | SARAVANAN |  | 15:15 | 16:05 | REPLACED TIMER AND LIGHT REPLACED | USED: HAGER TIMER 220V-1, T5 ROD LIGHT-2NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-09 | 16:23 | 120260265 | 120260146 | 1 | AMC | CAREEM | JADHAF | DXB | CHILLER CURTAIN ARE LOOSE | SARAVANAN |  | 17:10 | 18:10 | RE-FIX THE RIVET PROPERLY AND FIX THE PLASTIC CURTAIN |  |  | COMPLETED | WORK COMPLETED
2026-01-09 | 21:19 | 120260266 | 120260147 | 1 | AMC | CAREEM | AL QUOZ | DXB | DOOR LIMIT SWITCH DAMAGE | SADAM | MUTHUKUMAR | 22:20 | 23:15 | REPLACVE THE NEW LIMIT SWITCH AND UNIT WORKING NORMAL | USED: DOOE LIMIT SWITCH-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-09 | 10:05 | 120260267 | 7100289896 | 2 | AMC | ENOC | 305 | UMQ | CHILLER DOOR NOT CLOSING PROPERLY | AHSAN |  | 10:05 | 11:00 | SPRING TENSION INCREASED AND CLEAN THE DOOR HINGES OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-09 | 11:18 | 120260268 | 7100290315 | 2 | AMC | ENOC | 1057 | DXB | SUPPLY OF COLD ROOM DOOR HINGES FOR WALKIN | SADAM | MUTHUKUMAR |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 10JAN26
2026-01-09 | 20:11 | 120260269 | 7100290266 | 2 | AMC | ENOC | 1079 | DXB | PLASTIC CURTAIN IN WALKIN CHILLER | SADAM | MUTHUKUMAR | 20:35 | 21:05 | PVC CURTAIN DAMAGE NEED TO REPLACE | NEED: PVC CURTAIN 2MTR-2NOS |  | ATTENDED | NEED MATERIAL
2026-01-09 | 2:58 | 120260270 | 120260101 | 2 | WTY | ADNOC | 596 | FUJ | NOISY FUNCTION OF COND FAN MOTOR | RACEL | ROGER | 2:58 | 15:55 | REPLACED SCREW BOLT AND TIGHT PROPERLY, CLEAN THE CONDER COIL AND ALIGN THE CONDENSER LEVEL |  |  | COMPLETED | WORK COMPLETED
2026-01-09 | 19:00 | 120260271 | 120260130 | 2 | AMC | NESTO | WAREHOUSE | DXB | COMPRESSOR AREA ICE FORMATIONA AND WATER LEAK | SADAM | MUTHUKUMAR | 19:00 | 20:02 | FOUND COLD ROOM DOOR HANDLE ISSUE | NEED: DOOR HANDLE-1SET |  | ATTENDED | NEED MATERIAL
2026-01-09 |  | 120260272 | PPM | 37 | AMC | CAREEM | JVC PLAZA | DXB | PPM Q3 | ABID, AJMEER | RENJITH, SHAHABUDDIN |  |  | ALL UNIT CONDENSER CLEANED |  |  | COMPLETED | WORK COMPLETED
2026-01-09 |  | 120260273 | PPM | 37 | AMC | CAREEM | BB2 | DXB | PPM Q3 | GOVIND | ZALAUDDIN |  |  | ALL UNIT CONDENSER CLEANED AND UNIT CHECKED |  |  | COMPLETED | WORK COMPLETED
2026-01-09 |  | 120260274 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 8:00 | 22:00 | ADCOOP MUTEENA TRANSPORT, SHJ ACCOMADATION, CAREEM JLT TRANSPORT |  |  | COMPLETED | WORK COMPLETED
2026-01-10 | 8:33 | 120260275 | 120260148 | 1 | AMC | ANSAR | KARAMA | DXB | COLD ROOM WATER LEKA AND ICE FORMATION | MOHAMMED | SHABEEB | 10:55 | 13:45 | REMOVED THE ICE AND DAMAGE HETAER AND DRAIN HEATER REPLACED AND FIXED REWIRING | USED: DRAIN PIPE HEATER 6MTR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-10 | 8:39 | 120260276 | 120260149 | 2 | AMC | LULU | AL WATHBA | AUH | WATER LEAK AND LIGHT NOT WORKING | OLIVER | WILLIAM |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 11JAN26
2026-01-10 | 9:21 | 120260277 | 120260150 | 1 | AMC | LULU | AL AIN CENTER | AL AIN | JUICE CHILLER NOISE ISSUE | TALIB |  | 18:10 | 19:20 | FIX THE SCREW PROPERLY AND OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-10 | 9:46 | 120260278 | 120260151 | 1 | AMC | WESTLAND | AL AIN | AL AIN | CHILLER UNIT NOT WORKING | TALIB |  | 12:40 | 16:40 | LEAK ARRESTED IN BY CHANGING THE FLARE NOT AND CHARGED THE REF | USED: R404A-1 1/2 CYL BY WESTLAND |  | COMPLETED | WORK COMPLETED
2026-01-10 | 10:20 | 120260279 | 120260152 | 2 | PAYABLE | GRANDIOSE | AL SAHEL | AUH | JUICE CHILLER HIGH TEMP | RANDOLPH | TROVEE | 14:00 | 14:50 | FOUND COMPRESSOR HIGH AMPS DUE TO MECHANICAL ISSUE INTERNALLY | NEED: BITZER (4PES-15Y-40P), R404A-2CYL, SUNISO SL32-2GAL |  | COMPLETED | WORK COMPLETED | ON 14JAN26
2026-01-10 | 11:41 | 120260280 | 120260153 | 1 | AMC | ANSAR | KARAMA | DXB | VEG OPEN CHILLER WATER LEAK | MOHAMMED | SHABEEB | 10:55 | 13:45 | FLUSHED THE DRAIN LINE AND PASSAGE OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-10 | 15:55 | 120260281 | 120260155 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | CHILLER NAD FREEZER LIGHT NOT WORKING | MOHAMMED | SHABEEB | 15:55 | 16:30 | REPLACED THE LIGHTS AND WORKING NORMAL | USED: 4FT TUBE LIGHT-2NOS, 2FT TUBE LIGHT-2NOS |  | COMPLETED | WORK COMPLETED
2026-01-10 | 15:00 | 120260282 | 120260145 | 2 | AMC | LULU | SAADIYAT | AUH | FISH COLD ROOM HIGH TEMP ISSUE | RANDOLPH | TROVEE | 15:50 | 19:22 | REPLACED THE COMPRESSOR FILTER DRIER AND REPROCESS DONE | USD: COMPRESSOR, R404A, FILTER DRIER, SILFOS ROD-2 |  | COMPLETED | WORK COMPLETED
2026-01-10 | 9:00 | 120260283 | 120260115 | 2 | PAYABLE | GRANDIOSE | AL SOYOUH | SHJ | COLD ROOM FREEZER NOT WORKING | VIGNESH, SELVAN, SUDHEESH | RACEL, ROGER, ABIJITH | 9:00 | 2:00 | REPLACED THE FILTER DRIER AND CHECKED THE LEAK, NO LEAK FOUND, NITROGEN FLUSHING DONE | USED: R404A-2, BRAZING ROD-10, NITROGEN GAS-1, FILTER DRIER 3/8 FLARE-1, SENSOR-2 (NTC) |  | COMPLETED | WORK COMPLETED
2026-01-10 | 15:10 | 120260284 | 120260154 | 1 | WTY | ADNOC | 750 | FUJ | STELL BODY FREEZER NOT WORKING | RACEL | ROGER | 3:55 | 5:35 | RESET THE ELECTRICAL ISOLATOR SUPPY AND RESTARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-10 | 9:01 | 120260285 | 120260156 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | BUTCHERY AND CHEESE CHILLER NOT WORKING | OLIVER | WILLIAM | 18:00 | 19:43 | FOUND UNIT NORMAL OPERATION / JUICE CHILLER LOW REF, CHARGED REF AND STARTED THE UNIT WORKING NORMAL | USED: R22-1.5CYLS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-10 | 9:55 | 120260286 | 120260157 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | FREEZER HIGH TEMP | RANDOLPH | TROVEE | 21:50 | 23:05 | SWITCH OFF THE UNIT AND REMOVED THE COVER OF EVP. ICE FORMATION REMOVED AND STARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-10 | 11:19 | 120260287 | 120260158 | 1 | AMC | AD COOP/DEYAAR | MUROOR | AUH | GAS LEAK IN THE CHEESE SECTION | OLIVER |  | 13:28 | 15:55 | REPAIR THE DAMAGED CAPILARY TUBE AND EXPANSION VALVE. ADDITIONAL CHARGDE REF AND RESTARTED THE UNIT WORKING NORMAL | USED: R22-3CYLS, SILFOS ROD-1 |  | COMPLETED | WORK COMPLETED
2026-01-10 | 7:14 | 120260288 | 120260159 | 1 | AMC | TCS | SAFA PARK | DXB | FREEZER HIGH TEMP | SHAFI | MUSTAFA | 9:20 | 13:00 | CLENAED THE ICE BY MANUAL DEFROST AND CLENAED THE CONDENSER. REMOVED THE ONE CONDENSER FAN MOTOR FOR REPAIR | NEED: FAN MOTOR (S6D800) |  | ATTENDED | NEED MAGTERIAL
2026-01-10 | 9:17 | 120260289 | 120260011 | 2 | AMC | TCS | DEC MARINA | DXB | BACK STORE FREEZER TEMP ISSUE / ICE CREAM FREEZER CABINET WATER LEAK | SARAVANAN |  | 10:15 | 12:30 | REPLACED THE BOX FAN MTOR | USED: 120*120CM FAN MOTOR-5NOS, 1.5MM*3C WIRE-5MTR, WIRE CONNECTOR-2NOS |  | COMPLETED | WORK COMPLETED
2026-01-10 | 13:04 | 120260290 | 120260160 | 1 | AMC | TCS | FALCON KHALIDIYA | AUH | BAKERY CHILLER DISPLAY HIGH TEMP FREEZER CABINET HIGH TEMP (CHICKEN SECTION) | OLIVER | FROILAN, WILLIAM | 17:30 | 20:25 | CHARGED REF DUE TO LOW REF AND WORKING NORMAL / FREEZER ICE REMOVED BY MANUAL DEFROST AND FOUND DEFROST TIMER MALFUNCTION | USED: R404A BY BRANCH / NEED: DEFROST TIMER 220VAC-1, |  | ATTENDED | NEED MATERIAL
2026-01-10 | 8:31 | 120260291 | 120260161 | 1 | AMC | NESTO | MUWAILHA | SHJ | ICE MACHINE NOT WORKING | AHSAN |  | 14:45 | 16:05 | REPLACED THE FUSE AND START THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-10 | 18:00 | 120260292 | 120260162 | 1 | AMC | NESTO | AJG | AJM | FREEZER, DELICATE, BUTCHERY OPEN CHILLER LIGHT REPLACEMENT / FREEZER LIGHTS AND DELICATE LIGHTS | AHSAN | ABIJITH | 18:00 | 21:30 | REPLACED LIGHTS AND UNIT WORKING NORMAL / ELECTRONIC BALLAST AND LIGHTS NEED TO REPLACE | USED: HOLDER 2"-2NOS, T5 LED LIGHT-8NOS, T5 4FEET-6NOS, T5 2FT02NOS, T5 1FT-4NOS, T5 5FT-9NOS, T8 FT-2NOS / NEED: ELECTRONIC BALLAST-5NOS, 2FT T5 LED SET-2NOS, T8 LED 4FT-2NOS |  | COMPLETED | WORK COMPLETED
2026-01-10 | 13:00 | 120260293 | 7100290533 | 2 | AMC | ENOC | 305 | UMQ | FREEZER DRAIN LINE PIPE WATER LEAKING | SABITH ALI | LORIMER |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 12JAN26
2026-01-10 | 13:00 | 120260294 | 7100290628 | 1 | AMC | ENOC | 1036 | DXB | OPEN CHILLER SHELVES RUSTED | SADAM | MUTHUKUMAR | 18:40 | 19:30 | NEED TO REPAINT ALL THE SHELVES |  |  | ATTENDED | NEED TO REPAINT
2026-01-10 | 16:20 | 120260295 | 7100290641 | 1 | AMC | ENOC | 1079 | DXB | WALKIN CHILLER PLASTIC CURTAIN | SARAVANAN |  | 16:20 | 17:25 | REPLACED PLASTIC CURTAIN NEWLY | USED: 2MTR PLASTIC CURTAIN-2NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-10 | 22:00 | 120260296 | 7100290315 | 2 | AMC | ENOC | 1057 | DXB | SUPPLY OF COLD ROOM DOOR HINGES FOR WALKIN | SADAM | MUTHUKUMAR | 22:00 | 1:00 | REMOVED THE DAMAGED DOOR HINGES AND REPLACED | USED: DOOR HINGES-2 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-10 |  | 120260297 | PPM | 37 | AMC | TCS | PALM SHORELINE | DXB | PPM | GOVIND | ZALAUDDIN |  |  | ALL UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-10 |  | 120260298 | PPM | 37 | AMC | CAREEM | UMS | DXB | PPM Q3 | ABID, AJMEER | RENJITH, SHAHABUDDIN |  |  | ALL UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-10 |  | 120260299 | PPM | 37 | AMC | CAREEM | JVC LUNA | DXB | PPM Q3 | ZALAUDDIN |  |  |  | ALL UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-10 |  | 120260300 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 9:10 | 18:05 | DIP1, ABU DHABI AIR PORT DROP AND WAREHOUSE MATERIAL DELIVERY, ENOC 1079 MEATERIAL DELIVERY, CAREEM JLT UNIT PULL-OUT |  |  | COMPLETED | WORK COMPLETED
2026-01-11 | 9:12 | 120260301 | 120260163 | 1 | AMC | ANSAR | KARAMA | DXB | CHILLER ROOM ICE FORMATION | SARAVANAN |  | 13:30 | 14:20 | COLD ROOM ICE REMOVED, NEED TO CHANGE DOOR FULL SET | NEED TO REPLACE DOOR |  | ATTENDED | NEED TO REPLACE DOOR
2026-01-11 | 10:07 | 120260302 | 120260149 | 2 | AMC | LULU | AL WATHBA | AUH | WATER LEAK AND LIGHT NOT WORKING | OLIVER | WILLIAM | 10:07 | 10:40 | REMOVED THE WTAER AND CLEAN THE DRAIN PIPE / LIGHT FOUND DEFECTIVE / LED DRIVE DEFECTIVE | NEED: LED LIGHT 24V-1NO, LED DRIVE 24V-1 |  | ATTENDED | NEED MATERIAL
2026-01-11 | 10:45 | 120260303 | 120260164 | 2 | AMC | HOP | JEBAL ALI | DXB | COLD ROOM DOOR NOT CLOSING | SARAVANAN |  | 11:31 | 12:01 | REMOVED THE ICE FROM THE FLOOR AND FOUND HEATER DEFECTIVE | NEED: DOOR FRAME HEATER-1 (142*202CM) WIRE TYOE |  | ATTENDED | ATTENDED ON 24/1/2026
2026-01-11 | 10:58 | 120260304 | 120260165 | 1 | AMC | ANSAR | KARAMA | DXB | READY TO EAT SECTION LIGHT NOT WORKING | SARAVANAN |  | 13:30 | 14:20 | HOT FOOD LIGHT REPLACED | USED: 4FT LED LIGHT-1NO BY TD |  | COMPLETED | WORK COMPLETED
2026-01-11 | 15:33 | 120260305 | 120260166 | 2 | AMC | LULU | OLIVE TOWER | AUH | FREEZER ROOM TUBE LIGHTR NOT WORKING | OLIVER | FROILAN, WILLIAM |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 16JAN26
2026-01-11 | 16:00 | 120260306 | 120260167 | 1 | AMC | CAREEM | BB2 | DXB | FREEZER CABINET NOT WORKING PROPERLY | SHAFI | MUSTAFA | 16:00 | 16:30 | REMOVED THE SHELVES LABEL FROM THE RETURN AIR |  |  | COMPLETED | WORK COMPLETED
2026-01-11 | 18:23 | 120260307 | 120260168 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHARJAH | ICE CREAM FREEZER NOT WORKING | MOHAMMED | MUTHUKUMAR | 19:30 | 21:55 | REMOVED THE DAMAGE CONTCATOR AND FIXED. NEED TO REPLACE PHASE FAILYRE & TIME RELAY | USED: MAG CONTACTOR LC1D40AM7)-1 BY TD / NEED: PHASE FAILURE RM17TG-1, TIME DELAY-1NO |  | COMPLETED | WORK COMPLETED
2026-01-11 | 10:27 | 120260308 | 120260169 | 2 | AMC | AD COOP/DEYAAR | MBZ | AUH | COMBI FREEZER HIGH TEMP | OLIVER | WILLIAM | 11:07 | 12:25 | FOUND SYSTEM UNDERCHARGE AND LEAK FOUND IN ACCESS VALVE, ARRESTED THE LEAK AND CHARGED REF. NEED TO CHARGED MORE REF | USED: R404A-2 / R404-5CYLS, FAN MOTOR 16W-1NO |  | COMPLETED | WORK COMPLETED | ON 11JAN26
2026-01-11 | 12:28 | 120260309 | 120260170 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | DXB | FRUITS DISPLAY CHILELR NOT COOLING / CHILLER STORE WATER LEAK | OLIVER | FROILAN, WILLIAM | 14:37 | 16:30 | VEG CHILLER ICE FORMATION REMOVED BY HOT WTAER AND ADJUST THE DEFROST SETTING / COLD ROOM LEAK REMOVED THE ICE FORMATION |  |  | COMPLETED | WORK COMPLETED
2026-01-11 | 17:17 | 120260310 | 120260169 | 2 | AMC | AD COOP/DEYAAR | MBZ | AUH | COMBI FREEZER HIGH TEMP - REPLACE,ENT OF FAN MOTOR AND REF CHARGING | OLIVER | FROILAN, WILLIAM | , 17:17:00 | 18:28 | REPLACED THE DEFECTIVE FAN MOTOR AND CHARGED THE REF AND UNIT WORKING NORMAL | NEED: R404-5CYLS, FAN MOTOR 16W-1NO |  | COMPLETED | WORK COMPLETED
2026-01-11 | 19:15 | 120260311 | 120260171 | 1 | AMC | AD COOP/DEYAAR | MBZ | AUH | FREEZER NOT WORKING COMPRESSOR ROOM ABNORMAL NOISE ISSUE | OLIVER | WILLIAM | 20:26 | 23:05 | F19 FREEZER SLIDE GLAS DOOR NOT CLOSED PROPERLY AND ICE BUILD UP, REMOVED THE ICE FORMATION / MOTOR COMPRESSOR MINOR VIBRATION ITS NORMAL / FAN BLADE HITS THE ICE FORMATIO AND REMOVED THE ICE FORMATION. RESTARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-11 | 19:29 | 120260312 | 120260172 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | F#10 & F#11 FREEZER TEMP NOT GOOD | OLIVER | WILLIAM | 23:28 | 23:57 | FOUND UNIT NORMAL OPERATION |  |  | COMPLETED | WORK COMPLETED
2026-01-11 | 12:18 | 120260313 | 120260173 | 1 | AMC | TCS | SHOROOQ | DXB | FISH CHILLER NOT WORKING | SARAVANAN |  | 16:30 | 18:15 | FOUND CONTROLLER DEFECTIVE, REPLAVCED NEW CONTROLLER AND TEMP NORMAL | USED: CAREL CONTROLLER-1SET BY TD |  | COMPLETED | WORK COMPLETED
2026-01-11 | 21:20 | 120260314 | 120260174 | 1 | AMC | TCS | FALCON KHALIDIYA | AUH | BAKERY CHILLER NOT WORKING | RANDOLPH | TROVEE |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 12JAN26
2026-01-11 | 8:38 | 120260315 | 120260175 | 1 | AMC | NESTO | FUJAIRAH MALL | FUJ | WATER LEAK FROM THE INSULATION | VIGNESH | SELVAN | 17:40 | 19:00 | FOUND OUT THE COMPLAINT INSULATION DAMAGE, NEED TO REPLACE THE INSULATION | USED: INSULATION 3 5/19-2NOS, INSULATION 1 1/8-4, BISON KIT-1, SILICON-4, FOAM SPRAY-1, FOAM TAPE-3NOS |  | COMPLETED | WORK COMPLETED
2026-01-11 | 11:47 | 120260316 | 120260176 | 1 | AMC | NESTO | AL AIN CENTER | AL AIN | BAKERY CHILLER NOT WORKING | TALIB |  | 12:20 | 14:05 | REPKLACED THE DEFECTIVE FUSE AND UNIT WORKING NORMAL | USED: 13AMPS FUSE-1 BY STORE |  | COMPLETED | WORK COMPLETED
2026-01-11 | 7:06 | 120260317 |  | 0 | AMC | ENOC | 1009 | DXB | OPEN CHILLER NOT WORKING | SHAFI | MUSTAFA | 10:45 | 14:30 | LEAK FOUND OUT ON CONDENSER COIL U BEND, REPAIRED THE LEAK BY WELDING. VACUUM THE UNIT AND CHARGED THE REF UNIT WORKING NROMAL | NEED: CDU UNIT-1 |  | COMPLETED | WORK COMPLETED
2026-01-11 | 11:47 | 120260318 |  | 0 | AMC | ENOC | 1401 | RAK | WALKIN CHILLER NOISE ISSUE | VIGNESH | SELVAN | 14:50 | 15:30 | EVP COIL ICE REMOVED AND MANUALLY DEFROST, UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-11 | 17:01 | 120260319 |  | 0 | AMC | ENOC | 1062 | DXB | BED FREEZER NOT WORKING | MOHAMMED | MUTHUKUMAR | 22:45 | 3:10 | FREEZER AND EVP COIL FULL WATER SERVICE, REMOVED THE ICE FORMATION AND DRAIN LINE FLUSHING |  |  | COMPLETED | WORK COMPLETED
2026-01-11 | 7:00 | 120260320 |  | 0 | AMC | ENOC | 1036 | DXB | WALKIN FREEZER INSULATION DAMAGE | BIJU | GOVIND, ZALAUDDIN | 20:30 | 21:01 | PUMP DOWN THE UNIT, FREEZER PIPE ICE MELTED. FIXED THE INSULATION NEW AND OKAY. | USED: INSULATION 7/8-15NOS, BISON KIT-2CAN |  | COMPLETED | WORK COMPLETED
2026-01-11 | 2:36 | 120260321 | 5000215834 | 1 | AMC | ENOC | 1086 | ENOC | WALKIN CHILLER NOT WORKING | MOHAMMED | MUTHUKUMAR | 3:45 | 4:50 | WIRING AREA MOISTURED COVERED UP, DUE TO THAT UNIT TRIP. DRY OUT THE WIRING SIDE AND RESET THE ELCB WORKING NROMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-12 | 12:38 | 120260322 | 7100290851 | 1 | AMC | ENOC | 1027 | ENOC | WALKIN FREEZER DOOR NOT CLOSING | SARAVANAN | [6 empty] | COMPLETED
2026-01-12 | 12:38 | 120260323 | 7100290861 | 2 | AMC | ENOC | 1079 | DXB | NOISY SOUND FROM FOOD BENCH FREEZER | SARAVANAN | ZALAUDDIN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 13JAN26
2026-01-12 | 12:38 | 120260324 | 7100290862 | 2 | AMC | ENOC | 1079 | DXB | ICE FORMATION IN WALKIN FREEZER | SARAVANAN | ZALAUDDIN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 13JAN26
2026-01-12 | 12:38 | 120260325 | 7100290867 | 1 | AMC | ENOC | 1080 | DXB | WALKIN FREEZER ICE FORMATION | MOHAMMED | MUTHUKUMAR | 12:45 | 16:05 | DEFECTIVE DRAIN HETAER AND TRAY WITH NEED TO INSULATION | NEED: DRAIN TRAY HEATER (149CM)-1, DRAIN PIPOE HEATER 6MTR-1, 1/2" INSULATION-3NOS, BLACK TAPE 2"-2NOS |  | ATTENDED | NEED MATERIAL
2026-01-12 | 12:38 | 120260326 | 7100290868 | 1 | AMC | ENOC | 1094 | DXB | PRONTO FREEZER TEMP SHOWING -0.4 | SADAM |  | 13:15 | 13:30 | ADJUSTED THE DEFROST PARAMETER VALUE AND UNIT RUNNING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-12 | 12:38 | 120260327 | 7100290954 | 2 | AMC | ENOC | 1079 | DXB | FOOD BENCH CHILLER DOOR HANDLE | SARAVANAN | ZALAUDDIN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 13JAN26
2026-01-12 | 12:38 | 120260328 | 7100290956 | 1 | AMC | ENOC | 1072 | DXB | WALKIN FREEZER CURTAIN DAMAGED | SHAFI | MUSTAFA | [5 empty] | COMPLETED
2026-01-12 | 18:01 | 120260329 | 7100290533 | 2 | AMC | ENOC | 305 | UMQ | FREEZER DRAIN LINE PIPE WATER LEAKING | SABITH ALI | LORIMER | 20:14 | 21:05 | FIXED THE DRAIN PIPE PROPERLY AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-12 | 18:16 | 120260330 |  | 0 | AMC | ENOC | 1401 | RAK | WALKIN CHILLER NOISE ISSUE | SABITH ALI | LORIMER | [5 empty] | COMPLETED
2026-01-12 | 1:16 | 120260331 | 120260177 | 1 | AMC | ANSAR | KARAMA | DXB | LIGHTS NEED TO REPLACE FOR READY TO GO CHILLER | SADAM | ZALAUDDIN | 10:00 | 12:10 | REPLACED THE LIGHTS AND WORKING NORMAL | USEd: 4FT T8 TIBE LIGHT-2NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-12 | 10:14 | 120260332 | 120260178 | 2 | AMC | NESTO | WAREHOUSE | DXB | ICE MACHINE ISSUE / COMPRESSOR HAVE ICE FORMATION | AHSAN |  | 12:30 | 16:30 | WATER FLOW SWITCH TRIPPED, WATER SUPPLY PRESSURE SOMETIMES DROP. UNIT RESTARTED AND WORKING NORMAL / PLANT ROOM EVP ICE MELT AND START AGAIN AND CONDENSER BLOWER BELT NEED TO CHANGE | NEED: SPB4100 LA BELT-3NOS, GREASE-1 |  | COMPLETED | WORK COMPLETED | ON 16JAN26
2026-01-12 | 11:06 | 120260333 | 120260179 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER TRIPPING ISSUE | VIGNESH | SELVAN | 13:10 | 15:00 | FOUND HEATER DAMAGE AND ROCKER SWICTH FOR ON AND OFF | NEED: DRAIN PAN HEATER-1 (20CM), ON/OFF ROCKER SWITCH-1NOS |  | ATTENDED | NEED MATERIAL
2026-01-12 | 12:17 | 120260334 | 120260180 | 1 | AMC | BANIYAS COOP | SARAB | AUH | CAKE DISPLAY NEED TO CHECK | RANDOLPH | TROVEE | 16:00 | 17:00 | DISMATLED DEFECTIVE FAN MOTOR AND INSTALLED NEW | USED: EVP FAN MOTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-12 | 13:26 | 120260335 | 120260181 | 1 | AMC | CAREEM | DIERA | DXB | CHILLER CHILLER COLD ROOM HIGH TEMP | SARAVANAN |  | 16:30 | 22:00 | CLEAN THE OIL FILTER AND SYSTEM VACUUMIZED. RESTART THE SYSTEM NOW WORKING NORMAL | USED: SL32 OIL-1GAL BY TD |  | COMPLETED | WORK COMPLETED
2026-01-12 | 14:41 | 120260336 | 120260182 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | VEG CHILLER NOT COOLING | SADAM | GOVIND | 14:30 | 18:00 | FOUND LEAK IN THE PRIMARY COIL AND LEAK ARRESTED. CHARGED REF UNIT WORKING NORMAL | USED: R404A-1KG BY TD |  | COMPLETED | WORK COMPLETED
2026-01-12 | 17:35 | 120260337 | 120260183 | 2 | AMC | CAREEM | UMS | DXB | CHILELR DOORS NOT CLOSING PROPERLY | SARAVANAN | ZALAUDDIN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 13JAN26
2026-01-12 | 19:15 | 120260338 | 120260184 | 1 | AMC | NESTO | ARJAN | DXB | CHILLER CABINETS ARE NOT WORKING | MOHAMMED | MUTHUKUMAR | 23:00 | 24:10 | REPLACED THE DEFECTIVE MAG CONTACTOR FOR COMPRESSORN AND UNIT WORKING NORMAL | USED: MG CONTACTOR 32AMPS-1NO BY TD |  | COMPLETED | WORK COMPLETED
2026-01-12 | 11:16 | 120260339 | 120260186 | 1 | AMC | TCS | FALCON KHALIDIYA | DXB | CHILLER HIGH TEMP | FROILAN |  | 14:10 | 15:30 | UPON THE ARRIVAL UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-12 | 12:13 | 120260340 | 120260187 | 2 | AMC | TCS | DEC MARINA | DXB | FREEZER WATER LEAK | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 14JAN26
2026-01-12 | 6:16 | 120260341 | 120260188 | 3 | AMC | AD COOP/DEYAAR | MINA | AUH | FREEZER B38 NOT COOLING, ITEMS ARE MELTING | RANDOLPH |  | 10:45 | 12:10 | ICE UP DEFROST THE UNIT AND FOUND OUT MAGNETIC CONTACTOR DEFECTIVE, NEED TO REPLACE | NEED: CONTACTOR-1NO, SILICON WHITE-2NOS |  | ATTENDED | NEED MATERIAL
2026-01-12 | 9:36 | 120260342 | 120260189 | 1 | AMC | AD COOP/DEYAAR | HAMDAN | AUH | COLD ROOM ICE FORMATION / CHILLER HIGH TEMP | OLIVER | FROILAN, WILLIAM | 19:29 | 20:29 | ICE FORMATION REMOVED AND DUE TO AIR LEAK AND OKAY | USED: FOAM TAPE 2"-1NO |  | COMPLETED | WORK COMPLETED
2026-01-12 | 9:40 | 120260343 | 120260188 | 3 | AMC | AD COOP/DEYAAR | MINA | AUH | FREEZER#5 NOT COOLING | RANDOLPH | TROVEE | 9:40 | 12:30 | RELEASE THE PRESSURE OF COMPRESSOR, BRAZE THE LEAK IN THE PIPE AND VACUUM THE SYSTEM. CHARGED THE REF | USED: R404A BY ONTEGRA |  | COMPLETED | WORK COMPLETED
2026-01-12 | 9:40 | 120260344 | 120260188 | 3 | AMC | AD COOP/DEYAAR | MINA | AUH | FREZZER B38 NOT COOLING | RANDOLPH | TROVEE | 9:40 | 12:30 | REMOVED THE ICE FORMATION AND DISMANTLE DEFECTIVE CONTACTOR & REPLACED | USED: MAG CONTACTOR-1 BY ONGTEGRA |  | COMPLETED | WORK COMPLETED
2026-01-12 | 13:22 | 120260345 | 120260190 | 2 | AMC | AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | 3 CHILLER CABINET HIGH TEMP | VIGNESH | SELVAN | 15:50 | 17:50 | THERE IS LEAK NEED TO CHECK, TOMORROW SCHEDULE |  |  | COMPLETED | WORK COMPLETED | ON 13JAN26
2026-01-12 | 15:18 | 120260346 | 120260191 | 1 | AMC | AD COOP/DEYAAR | MUROOR | AUH | CHILLER ROOFTOP MAKING UNUSAL NOISE | OLIVER | WILLIAM | 17:08 | 18:35 | REPLACE THE FAN MOTOR AND UNIT IS RESTARTED THE UNIT WORKING NORMAL | USED: COND FAN MOTOR-1NO |  | COMPLETED | WORK COMPLETED
2026-01-12 | 21:00 | 120260347 | 120260192 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | YOGHURT JUICE AND VEG OPEN CHILLER HIGH TEMP | OLIVER | FROILAN, WILLIAM | 21:00 | 22:32 | LEAK ARRESTED AND CHARGED THE REF UNIT WORKING NORMAL | USED: R404A-1CYL, BLUE ROD-1NO |  | COMPLETED | WORK COMPLETED
2026-01-12 | 20:15 | 120260348 | 120260193 | 1 | AMC | NESTO | MALEHA | SHJ | CHILLER WATER LEAK AND CHILLER HIGH TEMP | SABITH ALI | LORIMER | 24:10 | 24:45 | MAIN DRAIN LINE BLOCKED DEDCLOGGED AND OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-12 | 18:16 | 120260349 |  | 0 | AMC | ENOC | 1401 | RAK | WALKIN CHILLER NOISE ISSUE | SABITH ALI | LORIMER | 21:40 | 23:15 | EVP FAN LEAF TOUCH IN EVP COIL, REMOVED THE ICE FORMATION AND OKAY AND ADJUSTED THE FAN MOTOR LEAF |  |  | COMPLETED | WORK COMPLETED
2026-01-12 | 24:51 | 120260350 |  | 0 | AMC | ENOC | 1099 | DXB | WALKIN FREEZER HIGH TEMP | SABITH ALI | LORIMER | 1:35 | 2:45 | FIXED ALL THE CABLES PROPERLY AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-12 |  | 120260351 | PPM | 37 | AMC | CAREEM | MARINA | DXB | PPM Q3 | SUDHEESH | ABIJITH |  |  | FREEZER AND CHILLER WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-12 |  | 120260352 | PPM | 37 | AMC | CAREEM | AL BARSHA | DXB | PPM Q3 | GOVIND | ZALAUDDIN |  |  | ALL FREEZER AND CHILELR CABINET WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-12 |  | 120260353 | PPM | 37 | AMC | CAREEM | DFC | DXB | PPM Q3 | ZALAUDDIN |  |  |  | WORKING NORMAL ALL UNITS |  |  | COMPLETED | WORK COMPLETED
2026-01-12 |  | 120260354 | DRIVING | 27 |  |  |  |  | DRIVING | WILLSON |  | 8:00 | 22:45 | AL BAZ MATERIAL COLLECTION, WAREHOUSE MATERIAL COLLECT AND DROP PPM TEAM IN CAREEM MARINA, COMPRESSOR DELIVERY IN TCS KHALIDIYA |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 8:58 | 120260355 | 120260194 | 2 | AMC | NESTO | SATWA | DXB | FREEZER NOT WORKING | SADAM |  | 9:30 | 15:15 | ELCB TRIPPING DUE TO FAN MTOOR WATER STAGANT, CLEANED THE DRAIN BLOCK AND REPLACED 2 FAN MOTOR AND UNIT WORKING NORMAL | USED: 10W FAN MOTOR-2NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-13 | 10:26 | 120260356 | 120260195 | 1 | AMC | NESTO | ARJAN | DXB | CHILLER NEED TO SERIVE AND CHECK THE PRESSURE | SHAFI | MUTHUKUAMR | 20:30 | 23:00 | CHILLER EVP AND COND COIL SERVICE DONE AND FIXED THE SENSOR IN ANOTHER LOCATION |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 11:39 | 120260357 | 120260196 | 1 | AMC | NESTO | KARAMA | DXB | DISPLAY FREEZER LIGHT NOT WORKING | SHAFI |  | 14:40 | 16:00 | UNIT FOUND TRIP OFF AND CHECKED ALL OKAY IN THE UNIT AND RESTART THE BREAKER WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 20:15 | 120260358 | 120260194 | 2 | AMC | NESTO | SATWA | DXB | FREEZER NOT WORKING | SABITH ALI | BIJU, LORIMER |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 14JAN26 | REPEAT COMPLAINT
2026-01-13 | 22:52 | 120260359 | 120260197 | 2 | AMC | NESTO | MAYSALOON | SHJ | BUTCHERY CHILLER TEAMP OKAY BUT ITEMS FROSTING | SABITH ALI |  |  |  | NOT ALLOWED TO WORK |  |  | NOT ATTENDED | SCHEDULE FOR 14JAN26
2026-01-13 | 24:17 | 120260360 | 120260198 | 1 | AMC | NESTO | WAREHOUSE | DXB | COMPRESSOR SHUTDOWN | MOHAMMED |  | 1:00 | 2:40 | CHECK THE CONTROLELR AND RESTARTED THE UNIT WORKING NROMAL, REST THE OIL PRESSURE AND UNIT WORKING NORMAL | NEED TO REPLACE CONDENSER BLOWER BELT AND FAN MOTOR BEARING |  | ATTENDED | NEED TO CHECK
2026-01-13 | 20:30 | 120260361 | 120260199 | 2 | AMC | NESTO | AJE | AJM | DELI CHILELR EVP COIL INSTALLATION | BIJU | LORIMER | 20:30 | 2:57 | PLACED THE EVP COIL AND FOUND NEED CAPLILARY TO BE REPLACE | NEED: CAPILARY TUBE 6M-1ROLL, ACCESS VALVE 1/4"-2NOS, FOAM SPRAY-1, SILICON-1 |  | COMPLETED | WORK COMPLETED
2026-01-13 | 14:06 | 120260362 | 120260200 | 1 | AMC | TCS | UMS | DXB | CHILLER WATER LEAK | MOHAMMED |  | 21:15 | 22:05 | REMOVED THE DRAIN LINE BLOCK AND FLUSHING. DRAIN PIPE TAPE |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 22:27 | 120260363 | 120260201 | 2 | AMC | TCS | LAKES | DXB | CHILELR COLD ROOM TEMP ISSUE | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 14JAN26
2026-01-13 | 1:35 | 120260364 | 120260202 | 2 | AMC | AD COOP/DEYAAR | SPAR SHABAT PLAZA | AL AIN | STORE FREEZER NOT WORKING | TALIB |  | 2:10 | 3:30 | FIX THE FUSE WITH WIRE AND NOW WORKING NORMAL | NEED: EVRC2L3A25C1 FAN MOTOR-1NO |  | ATTENDED | NEED MATERIAL
2026-01-13 | 1:57 | 120260365 | 120260203 | 3 | AMC | GRANDIOSE | AL SOYOUH | SHJ | COLOD ROOM MONOBLOCK UNIT NOT COOLING | AHSAN | RACEL |  | 1:57 | REVACUUM AND CHARGED THE REF USING SCALE AND TEMP -11 |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 10:30 | 120260366 | 120260183 | 2 | AMC | CAREEM | UMS | DXB | CHILELR DOORS NOT CLOSING PROPERLY | SARAVANAN | ZALAUDDIN | 11:00 | 12:00 | CLEAN THE DOOR WHEEL AND RAILING, APPLY THE GREESE WHEEL AND RAILING. CHILLER NO#6 LEFT SIDE DOOR NO HAVE SLIDING SPRING, NEED TO REPLACE | NEED TO REPLACE SLIDING DOOR SPRING |  | COMPLETED | WORK COMPLETED
2026-01-13 | 10:00 | 120260367 | 120260204 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER GALSS DAMAGE | VIGNESH | SELVAN | 10:00 | 12:40 | FIXED THE BAKERY CHILLER GLASS INSIDE PROPERLY | USED: WATER PROOF SILICON-4NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-13 | 14:38 | 120260368 | 120260205 | 1 | AMC | EVERMORE | DIP | DXB | UNIT 1 & 2 TEMP ISSUE | SHAFI | MUSTAFA | 18:00 | 19:15 | ADJUST THE TEMP IN THE CONTROLLER AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 10:30 | 120260369 | 120260206 | 1 | AMC | WESTLAND | AL AIN | AL AIN | GENERAL VISIT | TALIB |  | 11:45 | 15:00 | UNIT ALL WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 16:45 | 120260370 | 120260207 | 1 | WTY | CAREEM | BANIYAS | AUH | FREEZER COLD ROOM HIGH TEMP | OLIVER | FROILAN, WILLIAM | 17:27 | 21:00 | LEAK IN THE ACCESS VALVE ARRESTED, CHARGED REF | USED: R404A-1CYL BY TD |  | COMPLETED | WORK COMPLETED
2026-01-13 | 22:24 | 120260371 | 120260208 | 2 | WTY | CAREEM | MEYDAN | DXB | WALKIN FREEZER CONDENSATE PUMP WATER LEAK | MOHAMMED | MUTHUKUMAR | 15:30 | 16:00 | FOUND PUMP INSIDE WATER COVER AND GASKET DAMAGE, NEED TO REPLACE | NEED: CONDENSATE PUMP PC-125-1 |  | COMPLETED | WORK COMPLETED | ON 15JAN26
2026-01-13 | 12:30 | 120260372 | 120260190 | 2 | AMC | AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | DELICATE SECTION LEAK FIXING AND REFILLING GAS | AHSAN | ABIJITH | 12:30 | 22:30 | REPLACED THE FILTER DRIER DUE TO LEAK IN THE BODY, CHARGED THE REF AND UNIT WORKING NORMAL | USED: R404A-5CYL, 3/8 FILTER DRIER-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-13 | 11:16 | 120260373 | 120260209 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | FISH CHILLER WATER LEAK | RANDOLPH | TROVEE | 11:16 | 12:15 | FOUND DRAIN HEATER AND DISCONNECTED THE HEATER AND REPLACED THE DRAIN HEATER | NEED: DRAIN HEATER 230V-1NO |  | ATTENDED | NEED MATERIAL
2026-01-13 | 11:16 | 120260374 | 120260070 | 2 | AMC | AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER AND VEG FREEZER / BUTCHERY DISPLAY CHILLER HIGH TEMP | RANDOLPH | TROVEE | 11:16 | 12:15 | REMOVE THE UNIT BELOW THE CABINET DRAIN PIPE DECLOGGED AND CLEAN THE FAN GRILL AT BUTCHERY / FOUND FAN MOTOR DEFECTIVE | USED: 16-30W FAN MOTOR-1 |  | COMPLETED | WORK COMPLETED
2026-01-13 | 13:03 | 120260375 | 120260210 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | VEG CHILLER IS NOT WORKING | OLIVER | FROILAN, WILLIAM | 14:28 | 14:57 | ADJUST TEMP SET POINT, WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 13:47 | 120260376 | 120260211 | 1 | AMC | AD COOP/DEYAAR | MUROOR | AUH | F&V COLDR OOM FAN GUARD WITH HEAVY DUST ACCUMULATION NEED DEEP CLEANING | RANDOLPH | TROVEE | [5 empty] | COMPLETED
2026-01-13 | 22:21 | 120260377 | 120260212 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | F&V CHILLER NOT WORKING | FROILAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 14JAN26
2026-01-13 | 9:40 | 120260378 | 7100291336 | 1 | AMC | ENOC | 1138 | SHJ | OPEN CHILLER WATER LEAK | VIGNESH | SELVAN | 13:40 | 14:10 | OPEN CHILLER FOUND MAIN DRAIN LINE BLOCK |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 12:15 | 120260379 | 7100290861 | 2 | AMC | ENOC | 1079 | DXB | NOISY SOUND FROM FOOD BENCH FREEZER | SARAVANAN | ZALAUDDIN | 13:00 | 14:30 | REPLACED THE DEFRECTIVE COND FAN MOTOR, UNIT WORKING NORMAL | USED: 16W FAN MOTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-13 | 12:15 | 120260380 | 7100290862 | 2 | AMC | ENOC | 1079 | DXB | ICE FORMATION IN WALKIN FREEZER | SARAVANAN | ZALAUDDIN | 13:00 | 14:30 | FIXED THE DOOR GASKET PROPERLY AND CLENAED THE ICE. ADJUSTED THE TEMP |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 12:15 | 120260381 | 7100290954 | 2 | AMC | ENOC | 1079 | DXB | FOOD BENCH CHILLER DOOR HANDLE | SARAVANAN | ZALAUDDIN | 13:00 | 14:30 | REPAIRED THE DOOR HANDLE AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 15:36 | 120260382 |  | 0 | AMC | ENOC | 1086 | DXB | WALKIN CHILLER HIGH TEMP | SADAM |  | 16:30 | 19:10 | REPLACE THE NEW EVP FAN MTORO AND RUNNING NORMAL | USED: 16W FAN MOTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-13 | 12:57 | 120260383 | 7100291085 | 1 | AMC | ENOC | 1052 | DXB | bed freezer showing -14 temp | SARAVANAN |  | 16:45 | 16:50 | NOT OUR SCOPE |  |  | ATTENDED | NOT OUR SCOPE
2026-01-13 | 12:57 | 120260384 | 7100291135 | 3 | AMC | ENOC | 1511 | FUJ | 1 BUSTED LIGHTED LIGHT IN PRONTO DISPLAY | SABITH ALI |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 15JAN26
2026-01-13 | 12:57 | 120260385 | 7100291173 | 1 | AMC | ENOC | 1027 | DXB | DOOE GASKET DAMAGE CHILLER | SARAVANAN | ZALAUDDIN | 18:00 | 16:15 | NEED TO REPLACE CHILLER DOOR GASKET | NEED: 179*74.5CM GASKET - 10NOS |  | ATTENDED | NEED MATERIAL
2026-01-13 | 12:57 | 120260386 | 7100291176 | 2 | AMC | ENOC | 1080 | DXB | Walk in chiller fan not working /rusty | SADAM |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 14JAN26
2026-01-13 | 12:57 | 120260387 | 7100291179 | 1 | AMC | ENOC | 1072 | DXB | OPEN CHILLER WATER DRAINAGE REPAINT | SHAFI | MUSTAFA | [5 empty] | COMPLETED
2026-01-13 | 12:57 | 120260388 | 7100291180 | 1 | AMC | ENOC | 1072 | DXB | Wall in the counter area need to repaint | SHAFI | MUSTAFA | [5 empty] | COMPLETED
2026-01-13 | 12:57 | 120260389 | 7100291198 | 1 | AMC | ENOC | 507 | FUJ | Door Chiller having unnecessary sound ne | SABITH ALI |  | 22:30 | 22:50 | INSPECTED VERTICAL CHILLER NO ISSUE ALL WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-13 | 12:57 | 120260390 | 5000215856 | 1 | AMC | ENOC | 1027 | DXB | WALKIN FREEZER NOT COOLING | SARAVANAN | ZALAUDDIN | 18:00 | 18:15 | NEED: DOOR GASKET (179*74.5CM)-2NOS |  |  | ATTENDED | NEED MATERIAL
2026-01-13 | 21:41 | 120260391 | 7100291332 | 1 | AMC | ENOC | 1086 | DXB | WALKIN CHILLER HIGH TEMP | MOHAMMED | MUTHUKUMAR | 17:00 | 19:10 | FOUND EVP INSIDE |  |  | ATTENDED
2026-01-13 | 21:50 | 120260392 | 7100291328 | 1 | AMC | ENOC | 1080 | DXB | WALKIN FREEZER TEMP ISSUE -17 | SHAFI | MUSTAFA | 22:30 | 24:30 | TEMPORARY CLENAED THE ICE AND OPEN THE MAIN DRAIN LINE AND UNIT WORKING NORMAL | NEED TO CLEAN THE MAIN DRAIN LINE, NEED TO REMOVE THE ITEMS |  | ATTENDED | NEED MATERIAL
2026-01-13 |  | 120260393 | PPM | 37 | AMC | CAREEM | AL RAWDAH | AUH | PPM Q3 | OLIVER | FROILAN, WILLIAM |  |  | ALL UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-13 |  | 120260394 | PPM | 37 | AMC | CAREEM | AL RAHA | AUH | PPM Q3 | OLIVER | FROILAN, WILLIAM |  |  | ALL UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-13 |  | 120260395 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON | [6 empty] | COMPLETED
2026-01-14 | 10:00 | 120260396 | 120260213 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | B34 FREEZER NOT COOLING | OLIVER | WILLIAM | [5 empty] | COMPLETED
2026-01-14 | 8:40 | 120260397 | 1220250430 | 1 | AMC | AD COOP/DEYAAR | EMIRATES TOWER | AUH | F&V CHILLER NOISE ISSUE | RANDOLPH | TROVEE | 8:40 | 12:57 | REPLACED CPOMPRESSOR, FILTER DRIER AND REPROCESS DONE | USED: COMPRESSOR EMBRACO(NJP238GK)-1UNIT, FILTER DRIER 5/16-1, R404A-1, R141B-1, ACCESS VALVE 1/4-1, BLUE ROD-1, SILFOS ROD-2, NITROGEN-1 |  | COMPLETED | WORK COMPLETED
2026-01-14 | 13:18 | 120260398 | 120260214 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER COMPRESSOR READING NOT OKAY | RANDOLPH | TROVEE | [5 empty] | COMPLETED
2026-01-14 | 14:29 | 120260399 | 120260215 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | FREEZER B34 NOT COOLING / CHEESE CHILLER NOT COOLING | OLIVER | WILLIAM | 18:58 | 23:30 | MANUALLY DEFROST THE ICE FORM THE EVP, RELOCATED THE DEFROST SENSOR AND ADJUST THE DEFROST SETTING / CHILLER ICE FORMATION REMOBVED AND MANUAL DEFROST THE SYSTEMA ND UNIT DEFROST SETTING CHANGED |  |  | ATTENDED
2026-01-14 | 15:07 | 120260400 | 120260216 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | BAKERY CAKE CHILLER NOISE ISSUE | RANDOLPH | TROVEE | 19:40 | 20:00 | REPLACED THE DEFECTIVE FAN MOTOR AND FIXED THE SUPPLY | USED: 16-20W FAN MOTOR-1NO |  | COMPLETED | WORK COMPLETED
2026-01-14 | 15:09 | 120260401 | 120260217 | 1 | AMC | AD COOP/DEYAAR | AD MALL | AUH | F&V SECTION DISPLAY NOISY | FROILAN |  | 20:35 | 22:00 | ICE FORMATION REMOVED AND RESTARTED THE UNIT |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 17:06 | 120260402 | 120260218 | 1 | AMC | AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | FREEZER NOT COOLING | AHSAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 15JAN26
2026-01-14 | 19:12 | 120260403 | 120260212 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | F&V CHILLER NOT WORKING | FROILAN |  | 19:12 | 19:44 | UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 23:00 | 120260404 | 120260219 | 1 | AMC | AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | CABINET SHIFTING AND INSTALLATION | DENNIS, ROGER | SUDHEESH, ABIJITH | 23:00 | 7:30 | DISMANTLE CHILLER FRUIT & VEGETABLE, RELOVCATED AND LAYOUT PIPING CABINET OF PIPE. VACUUM AND ENERGIZED THE UNIT |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 9:04 | 120260405 | 120260220 | 2 | AMC | NESTO | AL AIN CENTER | AL AIN | HOT FOOD FOOD CHILLER HIGH TEMP / BUTCHERY CHILLER TEMP VARIATION AND FREEZER ITEMS MELTING | TALIB |  | 9:45 | 12:00 | CLEAN THE COND COIL AND TOP UP GAS / CHANGED THE SET POINT IN BUTCHERY CHILLER WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 9:35 | 120260406 | 120260221 | 1 | AMC | NESTO | AJC | AJM | FREEZER COLD ROOM LIGHT NOT WORKING | AHSAN |  | 16:30 | 18:30 | FREEZER COLD ROOM LIGHTS REPLACED |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 12:41 | 120260407 | 120260222 | 1 | AMC | NESTO | MUWAILHA | SHJ | FREEZER COLD ROOM TEMP ISSUE AND LIGHT NOT WORKING | BIJU | LORIMER | 19:00 | 2:00 | REMOVED THE 2 COLD ROOM EVP AND WATER SERVICE AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 14:31 | 120260408 | 120260223 | 1 | AMC | NESTO | AJC | AJM | ISLAND FREEZER SHUTDOWN | AHSAN |  | 16:30 | 18:30 | REMOVED THE MAIN SUPPLY AND CHECK ALL OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 12:30 | 120260409 | 120260199 | 2 | AMC | NESTO | AJE | AJM | DELICATE COUNTER UNIT#1 EVP FIXING | AHSAN |  | 12:30 | 15:50 | EVP COIL FIXED AND FLISH THE PIPE LINE, FILTER DRIER REPLACED AND UNIT WORKING NORMAL | USED: EVP COIL, R404-1, NITROGEN-1, 1/4 FILTER DRIER-1 |  | COMPLETED | WORK COMPLETED
2026-01-14 | 21:21 | 120260410 | 120260224 | 2 | AMC | NESTO | AJG | AJM | FREEZER TEMP NORMAL BUT NO COOLING | SABITH ALI | BIJU, LORIMER | 24:10 | 24:30 | PERMISSION AT 11AM TO CHECK THE UNIT |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 23:18 | 120260411 | 120260225 | 1 | AMC | NESTO | AL FAHIDI | DXB | ISLAND FREEXZER SHUTDOWN | SHAFI | MUSTAFA | 23:40 | 24:30 | CLEANED THE PCB BY BLOWER AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 23:10 | 120260412 | 120260197 | 2 | AMC | NESTO | MAYSALOON | SHJ | BUTCHERY CHILLER TEAMP OKAY BUT ITEMS FROSTING | SABITH ALI | BIJU, LORIMER | 23:10 | 23:45 | FIXED THE SENSOR PORPERLY AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 24:10 | 120260413 | 120260220 | 2 | AMC | NESTO | AL AIN CENTER | AL AIN | FREEZER#9 ITEMS MELTING | TALIB |  | 24:10 | 5:05 | REMOVE THE BOTH SIDE AND CHANGE THE EVP FAN MOTOR, WORKING NORMAL | USED: FAN MOTOR 5W-3NOS |  | COMPLETED | WORK COMPLETED
2026-01-14 | 6:45 | 120260414 | 120260201 | 2 | AMC | TCS | LAKES | DXB | CHILELR COLD ROOM TEMP ISSUE | SARAVANAN |  | 9:15 | 10:30 | TOP UP REF AND RESTARTED THE UNIT WORKING NORAML | USED: R22 BY STORE |  | COMPLETED | WORK COMPLETED
2026-01-14 | 6:41 | 120260415 | 120260202 | 2 | AMC | TCS | UMS | DXB | FREEZER HIGH TEMP | SADAM |  | 9:00 | 11:05 | CHECK LEAK NOT FOUND AND UNIT SWITCH ON ANDN TOP UP REF AND UNIT WORKING NORMAL | USED: R404A-1 BY STORE |  | COMPLETED | WORK COMPLETED
2026-01-14 | 11:30 | 120260416 | 120260187 | 2 | AMC | TCS | DEC MARINA | DXB | FREEZER WATER LEAK | SARAVANAN |  | 11:30 | 14:15 | FREEZER CABINET BOTTOM SIDE APPLIED SILICON AND CHILLER DRAIN BLOCK AND RECTIFIED AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 8:37 | 120260417 | 7100291501 | 1 | AMC | ENOC | 1127 | SHJ | WALKIN CHILLER HIGH TEMP | AHSAN |  | 10:30 | 11:30 | REMOVED THE DEFROST AND REACHED THE CUT OFF A=IN SET POINT AND CHANGED THE DEFROST SETTING |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 12:14 | 120260418 | 7100291293 | 2 | AMC | ENOC | ZOOM4002 | DXB | Busted lights chiller and selling area. | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 15JAN26
2026-01-14 | 12:14 | 120260419 | 7100291294 | 1 | AMC | ENOC | ZOOM4009 | DXB | water leak at chiller number 2. | SARAVANAN |  | 17:15 | 19:00 | DRAIN BLOCK CLEATED AND CHILLER#1 FLOAT SWITCH POOR CONDITION NEED TO REPLACE | NEED: FLOAT SWITCH-1 |  | ATTENDED | NEED MATERIAL
2026-01-14 | 12:14 | 120260420 | 7100291409 | 2 | AMC | ENOC | 509 | FUJ | ice formation on walk in freezer door | VIGNESH | SELVAN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 16JAN26
2026-01-14 | 12:14 | 120260421 | 7100291497 | 2 | AMC | ENOC | 508 | FUJ | CHILLER 1-5 DOWN COVER SHEET DETACHED | VIGNESH | SELVAN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 16JAN26
2026-01-14 | 12:14 | 120260422 | 7100291498 | 1 | AMC | ENOC | 1007 | DXB | Open Chiller temperature high | SHAFI | MUSTAFA | 18:10 | 19:45 | CHECK THE DEFROST SCHEUDLE, OPEN CHILLER PIPE INSULATION DAMAGE | NEED: INSULATION (22MM)-5NOS, 28MM-5NOS, GLUE-2NOS, TAPE-10NOS |  | ATTENDED | NEED MATERIAL
2026-01-14 | 12:14 | 120260423 | 7100291329 | 1 | AMC | ENOC | 1080 | DXB | Walk-in Freezer main drainage is clogged | SADAM |  | 13:30 | 18:40 | CLEANED THE MAIN DRAIN LINE AND OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 14:39 | 120260424 |  | 0 | AMC | ENOC | 1099 | DXB | WALKIN FREEZER HIGH TEMP | SARAVANAN |  | 15:30 | 16:45 | PROPERLY FIX THE WIRE AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 14:45 | 120260425 | 7100289710 | 2 | AMC | ENOC | 1052 | DXB | GASKET FOR WALKIN FREEZER DOOR, DAMAGE | SHAFI | MUSTAFA | 16:45 | 17:30 | REPLACED THE DAMAGED GASET WITH NOEW AND GASKET HOLDER | USED: GASKET HOLDER-2DOORS, GASKET-2DOORS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-14 | 13:30 | 120260426 | 7100291176 | 2 | AMC | ENOC | 1080 | DXB | Walk in chiller fan not working /rusty | SADAM |  | 13:30 | 18:40 | FOUND FAN MOTOR DEFECTIVE, REPLACED AND WORKING NORMAL | USED: 16W FAN MOTOR-1 BY TD | FAN GRLLS NEED TO REPAINT | COMPLETED | WORK COMPLETED
2026-01-14 | 12:12 | 120260427 | 120260226 | 1 | AMC | BAQER MOHEBI | AL NADHA | DXB | PORK FREEZER NOT WORKING | VIGNESH | SELVAN | 15:50 | 16:30 | CLENAED THE CONDENSER COIL AND PORK FREEZER WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-14 | 10:10 | 120260428 | 120260050 | 2 | AMC | BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER COMPRESSOR INSTALLATION | VIGNESH | SELVAN | 10:10 | 15:10 | COMPRESSOR AND FILTER DRIER REPLACED AND REPROCESS DONE | USED: COMPRESSOR (SC15MLX)-1, R404A-1, 1/4 FILTER DRIER SOLDER-1, NITROGEN-1, 16W FAN MOTOR-1 |  | COMPLETED | WORK COMPLETED
2026-01-14 | 16:23 | 120260429 | 120260227 | 1 | AMC | BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER HEAD NOT COOLING | VIGNESH | SELVAN | 17:00 | 22:30 | FOUND HP HOSE DAMAGE, REPLACE THE HOSE AND CHARGED REF | USED: HP HOSE-1, R22-2CYLS |  | COMPLETED | WORK COMPLETED
2026-01-14 | 17:15 | 120260430 | 1202606228 | 2 | AMC | ANSAR | KARAMA | DXB | BUTCHERY CHILLER WATER LEAK / LIGHT NOT WORKING IN THE READY TO GO CHILLER | SHAFI | MUSTAFA |  |  | CLEANED THE DRAIN LINE AND BUTCHERY CHILLER NEED TO CHANGE THE LIGHT AT THE CONNECTOR AND NORMAL TUBE NEED TO CHANGE WIRING | NEED: LED 4FT-3NOS |  | ATTENDED | NEED MATERIAL
2026-01-14 | 17:44 | 120260431 | 120260203 | 3 | PAYABLE | GRANDIOSE | AL SOYOUH | SHJ | COLD ROOM FREEZER NOT COOLING | DENNIS, ROGER | RACEL | 9:47 | 17:40 | FOUND HIGH PRESSURE DURING DEFROST, MALFUNCTION PCB BOARD. DAMAGED EVP FAN MOTOR | NEED: EVP FAN MOTOR (EVR2L3A25C)-1, ZANOTI PCB BOARD-1 |  | ATTENDED | NEED MATERIAL
2026-01-14 | 14:35:000 | 120260432 | 120260152 | 2 | PAYABLE | GRANDIOSE | AL SAHEL | AUH | JUICE CHILLER HIGH TEMP | RANDOLPH, TROVEE | OLIVER, FROILAN | 14:35 | 18:10 | DISMANTLED THE OLD COMPRESSOR AND REPLACED NEW COMPRESSOR. VACUUM THE SYSTEM AND START THE UNIT. CHARGED ADDITIONAL REF AND OIL | USED: BITZER (4PES-15Y-40P), R404A-2CYL, SUNISO SL32-2GAL |  | COMPLETED | WORK COMPLETED
2026-01-15 |  | 120260433 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 8:50 | 21:25 | DIP1 TRANSPORT, ALQUOZ MATERIAL COLLECTION, WARE HOUSE MATERIAL COLLECTION AND MEGAMART AL NADHA MATERIAL DELIVERY, AJC MATERIAL DELIVERY |  |  | COMPLETED | WORK COMPLETED
2026-01-15 | 9:00 | 120260434 | 120260229 | 1 | AMC | ANSAR | KARAMA | DXB | HOT FOOD CHILLER HIGH TEMP | SARAVANAN |  | 11:00 | 11:45 | CHECKED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-15 | 11:00 | 120260435 | 1202606228 | 2 | AMC | ANSAR | KARAMA | DXB | LIGHT REPLACEMENT IN READY TO GO CHILLER | SARAVANAN |  | 11:00 | 11:45 | LIGHT REPLACED | USED: 36W TUBE LIGHT-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-15 |  | 120260436 | 120260230 | 1 | AMC | AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | FREEZER TEMP ISSUE | AHSAN |  | 9:20 | 17:30 | REFILL THE OIL IN COMP#1 AND COMP#2 FIX THE OIL LEAK AND START THE UNIT AMD CLEAN THE CONDENSER OF CHILLER AND FREEZER | USED: SL32 OIL-2GAL, R404A-2CYL BY DEYAAR / NEED: XC811M DIXELL CONTROLLER-1 |  | ATTENDED | NEED MATERIAL
2026-01-15 | 18:46 | 120260437 | 120260231 | 1 | AMC | AD COOP/DEYAAR | JADHAF | DXB | FREEZER CABINET F1 TEMP HIGH | SHAFI | MUSTAFA |  | 18:45 | UNIT HAVE A LEAK AND NEED TO PULLOUT THE UNIT TO CHECK THE LEAK. THE EXISTING COMPRESSOR IS NOT SUITABLE, DUE TO ORIGINAL IS DIFFERENT |  |  | ATTENDED | NEED TO LEAK TEST
2026-01-15 | 19:00 | 120260438 | 120260208 | 2 | WTY | CAREEM | MEYDAN | DXB | WALKIN FREEZER CONDENSATE PUMP REPLACEMENT | MOHAMMED | MUTHUKUMAR | 20:00 | 21:20 | REMOVED THE DAMAGED PUMP AND REPLACED WITH NEW. WORKING NORMAL | USED: CONDENSATE PUMP (P180)-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-15 | 7:48 | 120260439 | 120260232 | 1 | AMC | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | FREEZER CABINETS ARE NOT WORKING | RACEL |  | 8:47 | 22:55 | CLEAN THE CONDENSER COIL AND REMOVED THE BLOCK FROM THE CONDENSER COIL AND START THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-15 | 8:09 | 120260440 | 120260233 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | B21 CHILLER NOISE ISSUE | RANDOLPH | TROVEE | 10:50 | 11:46 | DUE TO OVERLOAD OF ITEMS, INFOMRED THE STAFF TO LESS THE ITEMS ON THE LOADING TIME |  |  | COMPLETED | WORK COMPLETED
2026-01-15 | 8:40:l00 | 120260441 | 120260234 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | COMPRESSOR MAIN CONTROLLER HIGH READING DISPLAY | RANDOLPH | TROVEE | 20:40 | 9:52 | BREAKER OBVERLOAD DEFECTIVE, TEMPORARY CONNECTED IN CHILLER AREA, NEED TO REPLACE | NEED: BREAKER OVERLOAD SIEMENS-1 (SAMPLE GIVEN IN STORE) |  | ATTENDED | NEED MATERIAL
2026-01-15 | 19:43 | 120260442 | 120260235 | 1 | AMC | AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | VEG CHILLER NOT WORKING | MOHAMMED | MUTHUKUMAR | 22:20 | 23:35 | NEED TO INSTALL ISLOATOR, DUE TO UNIT HAVE 2 COMPRESSOR NO PROPER EFFICIENY. | NEED TO REPLACE ISOLATOR FROM DEAYAAR |  | ATTENDED | NEED MATERIAL
2026-01-15 | 22:14 | 120260443 | 120260236 | 3 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER RACK UNIT NOT WORKING | RANDOLPH | OLIVER | 23:00 | 24:35 | FOUND MAIN PANEL FREEZER RACK MCB DEFECTIVE, NEED TO REPLACE | NEED: MCB BREAKER-1 (NSX400N) |  | COMPLETED | WORK COMPLETED | ON 16DEC25
2026-01-15 | 23:28 | 120260444 | 120260237 | 1 | AMC | AD COOP/DEYAAR | BAIN AL JESSRAIN | AUH | FREEZER NOT WORKING, BUT POWER IS OKAY | RANDOLPH | TROVEE | 6:04 | 19:00 | TRIPPING ISSUE DUE TO DRAIN HEATER AND SHORTED, DISCONNECT THE DRAIN HEATER | NEED: DRAIN HEATER STRAIGHT ROD 25CM, 220V-1NO |  | ATTENDED | NEED MATERIAL
2026-01-15 | 2:40 | 120260445 | 120260236 | 3 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER RACK UNIT NOT WORKING | RANDOLPH | TROVEE | 2:40 | 5:44 | REPLACED THE MCB AND RESTARTED THE UNIT WORKING NORMAL | USED: MCB BREAKER-1 (NSX400N) | OLD BRAKER REPLACED | COMPLETED | WORK COMPLETED
2026-01-15 | 8:26 | 120260446 | 120260238 | 2 | AMC | ADNOC | 596 | FUJ | FREEZER HIGH TEMP AND ITEMS ARE MELTING | SABITH ALI | BIJU, LORIMER |  | 22:45 | FOUND ORIFICE DEFECTIVE, NEED TO REPLACE AND REPROCESS | NEED: ORIFICE#0-1, 1/4 SOLDER FILTER DRIER-1, R404A-1 |  | ATTENDED | NEED MATERIAL
2026-01-15 |  | 120260447 | DELIVERY | 1 | AMC | ADNOC | 511 | SHJ | HOT DOG GRILLER AND AND ROLLER DELIVERY | VIGNESH |  | 12:07 | 15:55 | DELIVERY DONE |  |  | COMPLETED | WORK COMPLETED
2026-01-15 | 10:41 | 120260448 | 7100291567 | 2 | AMC | ENOC | 2020 | DXB | BED FREEZER LIGHT NOT WORKING | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 18JAN26
2026-01-15 | 10:41 | 120260449 | 7100291569 | 1 | AMC | ENOC | 32 | DXB | OPEN CHILLER IN PRONTO AREA | SARAVANAN |  | 13:44 | 14:30 | CHECKED AND CLEAERD TH DRAIN LINE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-15 | 10:41 | 120260450 | 7100291639 | 1 | AMC | ENOC | 1016 | DXB | OPEN CHILLER LIGHT NOT WORKING | MOHAMMED | MUTHUKUMAR | 24:40 | 24:30 | REMOVED THE DAMAGE FUSE AND REPLACED. UNIT WORKING NORMAL | USED: FUSE-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-15 | 10:41 | 120260451 | 7100291644 | 3 | AMC | ENOC | 1022 | DXB | FREEZER CURTAIN IS DAMAGED | MOHAMMED |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED
2026-01-15 | 10:41 | 120260452 | 7100291693 | 1 | AMC | ENOC | 1032 | DXB | WALKIN FREEZER ICE FORMATION | MOHAMMED | MUTHUKUMAR | 1:00 | 2:00 | REMOVED THE ICE FORMATION AND CHECK THE HEATER ALL WORKING NORMAL AND ADJUST THE DEF SETTING |  |  | COMPLETED | WORK COMPLETED
2026-01-15 | 9:45 | 120260453 | 7100289130 | 2 | AMC | ENOC | 1033 | DXB | WALKIN FREEZER ICE - GASKET INSTALLATION | SADAM |  | 9:45 |  | REPLACED THE BOTTOM GASKET AND OKAY | USED: BOTTOM GASKET-2NO BY TD |  | COMPLETED | WORK COMPLETED
2026-01-15 | 15:11 | 120260454 | 7100291293 | 2 | AMC | ENOC | ZOOM4002 | DXB | Busted lights chiller and selling area. | SARAVANAN |  | 16:30 | 17:00 | REPLACED THE DEFECTIVE LIGHTS AND UNIT WORKING NORMAL | USED: 3FT LED LIGHT-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-15 | 18:08 | 120260455 | 7100291135 | 3 | AMC | ENOC | 1511 | FUJ | 1 BUSTED LIGHTED LIGHT IN PRONTO DISPLAY | SABITH ALI |  | 21:15 | 21:30 | NEED TO REPLACE LED TUBE | NEED: LED TUBE 2FT-1NO |  | ATTENDED | NEED MATERIAL
2026-01-15 | 9:24 | 120260456 | 120260239 | 1 | AMC | NESTO | AJC | AJM | ISLAND FREEZER NOT WORKING | RACEL | SELVAN | 12:23 | 16:40 | FOUND PARTIALLY GROAUND IN HANGING CONNECTOR AND ELECTRICAL BOX CABINET FREEZER#6 REMOVE THE GROUNDED THEN RESTARTED THE UNIT |  |  | COMPLETED | WORK COMPLETED
2026-01-15 | 9:34 | 120260457 | 120260108 | 3 | AMC | NESTO | AJC | AJM | ISLAND FREEZER NOT WORKING | RACEL | SELVAN | 12:23 | 16:40 | INSTALLED THE REPAIRED THE 2 CONDENSER FAN MOTOR | USED: COND FAN MOTOR-2NOS |  | COMPLETED | WORK COMPLETED
2026-01-15 | 19:59 | 120260458 | 120260224 | 2 | AMC | NESTO | AJG | AJM | FREEZER TEMP NORMAL BUT NO COOLING | SABITH ALI | BIJU, LORIMER | 24:20 | 2:30 | CLEANED THE EVP COIL AND DRAIN SECTION PIPE AND REMOVED THE ICE FORMATION. RESTARTED THE DISPLAY FREEZER CABINET |  |  | COMPLETED | WORK COMPLETED
2026-01-15 | 21:41 | 120260459 | 120260240 | 2 | AMC | NESTO | AJF | AJM | DELI CHILLER HIGH TEMP ISSUE | SABITH ALI |  | 12:40 | 1:15 | NEED TO TOP UP GAS | NEED: R134A |  | COMPLETED | WORK COMPLETED | ON 16JAN2026
2026-01-15 |  | 120260460 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  |  |  | FAWAS COMPRESSOR FROM PASONS 28 COMPRESSOR, DIERA MATERIAL COLLECTION AND DELIVERY |  |  | COMPLETED | WORK COMPLETED
2026-01-15 |  | 120260461 | DRIVING | 27 |  |  |  |  | DRIVING | GOVINTH |  |  |  | ARAVIND HOSPITAL PICK UP AND DROP, MATERIAL FROM WAREHOUSE AND DELIVERY IN SHARJAJ TO DENNIS |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 8:29 | 120260462 | 120260241 | 1 | WTY | NESTO | MUWAILHA | SHJ | CHEESE CHILLER HIGH TEMP | VIGNESH | SELVAN | 9:20 | 11:00 | REPLACVED THE DEFECTIVE BOX FAN MOTOR AND RESTARTED THE UNIT WORKING NORMAL | USED: BOX FAN MOTOR 120*120-1NO |  | COMPLETED | WORK COMPLETED
2026-01-16 | 10:44 | 120260463 | 120260240 | 2 | AMC | NESTO | AJF | AJM | DELI CHILLER HIGH TEMP ISSUE | AHSAN |  | 11:20 | 12:30 | REF CHARGED AND UNIT WORKING NORMAL TEMPORARY / NEED TO CHECK LEAK | USED: R134A BY NESTO / NITROGEN-1, 1/4 FILTER DRIER FLARE TYPE-1 |  | ATTENDED | NEED MATERIAL
2026-01-16 | 24:00 | 120260464 | 120260242 | 1 | AMC | NESTO | AL MINA | DXB | HOT FOOD CHILLER TEMP ISSUE | SADAM | ZALAUDDIN | 15:00 | 16:30 | CLEAN THE CONDENSER COIL AND CHILLER RESTARTED WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 2:14 | 120260465 | 120260243 | 1 | AMC | LULU | NUAIMIA | AJM | EGG CHILLER GETTING NEGATIVE TEMP | AHSAN |  | 9:00 | 10:30 | CHANGE THE SET POINT AND CHECK THE PARAMETERS ALL OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 9:41 | 120260466 | 120260244 | 1 | AMC | ANSAR | KARAMA | DXB | COMBI FREEZER WATER LEAK | SADAM | ZALAUDDIN | 16:50 | 18:40 | REPAIR THE DRAIN PIPE AND LEAK FIXED |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 8:30 | 120260467 | 120260245 | 1 | AMC | GRANDIOSE | AL SAHEL | AUH | CHILLER UNIT NOT WORKING | OILVER | FROILAN, WILLIAM | 9:48 | 16:19 | REPLACED THE OIL AND CHARGED REF UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 16:47 | 120260468 | 120260246 | 1 | AMC | LULU | DIP | DXB | FREEZER NOISE ISSUE | MOHAMMED | MUTHUKUMAR | 1:40 | 3:00:000 | PUT THE UNIT IN MANUAL DEFROST AND MELTED THE ICE | IF AGAIN SAME ISSUE NEED TO CLEAN THE EVP COIL |  | COMPLETED | WORK COMPLETED
2026-01-16 | 16:50 | 120260469 | 120260247 | 2 | AMC | BAQER MOHEBI | ABU HAIL | DXB | CDU#6 FAN MOTOR NOT WORKING | SABITH ALI | BIJU, LORIMER | 20:10 | 20:40 | FOUND COND FAN MTOOR DEFECTIVE, NEED TO REPLACE | NEED: EBM 4E-500, 220V-1NO |  | COMPLETED | WORK COMPLETED | ON 20JAN26
2026-01-16 | 19:17 | 120260470 | 120260248 | 1 | AMC | LULU | MAQAM | AL AIN | FISH COLD ROOM CHILLER LIGHT NOT WORKING | TALIB |  | 19:40 | 21:15 | CHECK THE CHILLER LIGHT TUBE DAMAGE AND NEED TO REPLACE | NEED: LED TUBE LIGHT 4FT-2NOS (MILANO) WATER PROOF |  | ATTENDED | NEED MATERIAL
2026-01-16 | 19:25 | 120260471 | 120260166 | 2 | AMC | LULU | OLIVE TOWER | AUH | COLD ROOM FREEZER BUSTED LIGHT | OLIVER | FROILAN, WILLIAM | 19:25 | 19:34 | REPLACED THE COLD ROOM LIGHTS AND WORKING NORMAL | USED: 4FT LED LIGHT-2NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-16 | 20:54 | 120260472 | 120260249 | 1 | AMC | CAREEM | MARINA | DXB | CHILLER SHUTDOWN | MOHAMMED | MUTHUKUMAR | 23:00 | 23:58 | REPLACED THE MAIN POWER SOCUKET AND PLUG, UNIT RESTARTED AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 19:30 | 120260473 | 120260178 | 2 | AMC | NESTO | WAREHOUSE | DXB | RACK SYSTEM CONDENSER BLOWER BELT REPLACEMENT | MOHAMMED | MUTHUKUAMR | 19:30 | 21:45 | REPLACED THE BELTS AND GREASED THE BEARINGS AND OKAY | USED: SPB4100 LA BELT-3NOS, GREASE-1 |  | COMPLETED | WORK COMPLETED
2026-01-16 | 8:00 | 120260474 | 7100285529 | 1 | AMC | ENOC | 1039 | DXB | ICE FORMATION IN WALKIN FREEZER | SADAM |  | 8:30 | 11:00 | REPLACE THE DAMAGE INSULATION AND OKAYB | USED: 5/8 INSULATION-1, 2" BLACK TAPE-2, FOAM TAPE-1 |  | COMPLETED | WORK COMPLETED
2026-01-16 | 12:04 | 120260475 | 7100291768 | 1 | AMC | ENOC | 412 | RAK | Spray painting of existing shelves insid | SABITH ALI | BIJU, LORIMER | 22:15 | 22:45 | ALTERNATE POSITION FOUND OFR FREEZER AND NEED TO INSTALL ELECTRICAL PLUG POINT ON FREEZER AREA | NEED PLUG POINT IN FREEZER AREA |  | COMPLETED | WORK COMPLETED
2026-01-16 | 12:04 | 120260476 | 7100291835 | 1 | AMC | ENOC | 1401 | RAK | deli chiller need to check for sandwich | SABITH ALI | BIJU, LORIMER | 23:15 | 23:50 | TOP SIDE FAN MOTOR PROTECTION SHEETS IS RUSTED AND DAMAGE, NEED TO REPLACE THE FAN MOTOR AND FAN MOTOR PROTECTION SHEET | NEED: AXIAL FAN 120*120-2NOS, SS PROTECTION SHEET-2NOS (SAMPLE HAS TAKEN) |  | ATTENDED | NEED MATERIAL
2026-01-16 | 12:04 | 120260477 | 7100291839 | 1 | AMC | ENOC | 1071 | DXB | Walk in chiller is not working properly | SADAM |  | 13:15 | 14:15 | ADJUST THE DEFROST PARAMATER VALVE AND UNIT RUNNING NORMAL | WALKIN CHILLER DOOR NEED RO REPAINT AND NEED TO PAINT OPEN CHILLER DRAINAGE |  | COMPLETED | WORK COMPLETED
2026-01-16 | 12:04 | 120260478 | 7100291867 | 2 | AMC | ENOC | 1088 | DXB | Walking freezer ice formation | SADAM |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 16JAN26
2026-01-16 | 12:04 | 120260479 | 7100291870 | 2 | AMC | ENOC | 1041 | DXB | Walk in chiller bulb light 4 nos. busted | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 17JAN26
2026-01-16 | 12:04 | 120260480 | 7100291888 | 2 | AMC | ENOC | 1012 | DXB | Walk in chiller ceiling lights are buste | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 17JAN26
2026-01-16 | 12:04 | 120260481 | 7100291941 | 2 | AMC | ENOC | 1056 | DXB | vertical freezer 1 light busted | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 18JAN26
2026-01-16 | 12:04 | 120260482 | 7100291961 | 2 | AMC | ENOC | ZOOM4009 | DXB | chiller 3 water leaking | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 17JAN26
2026-01-16 | 11:40 | 120260483 | 7100277439 | 1 | AMC | ENOC | 1007 | DXB | WALKIN CHILLER DOOR#4 RUBBER LINING | SADAM |  | 11:40 | 12:30 | REPLACE THE WALKIN CHILLER GLASS DOOR GASKET AND WORKING NROMAL | USED: DOOR GASKET-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-16 | 13:45 | 120260484 | 7100291409 | 2 | AMC | ENOC | 509 | FUJ | ice formation on walk in freezer door | VIGNESH | SELVAN | 13:45 | 14:15 | FOUND WALKIN FREEZER DOOR GASKET IS DAMAGE, NEED TO REPLACE | NEEd: DOOR GASKET-15MTR |  | ATTENDED | NEED MATERIAL
2026-01-16 | 12:55 | 120260485 | 7100291497 | 2 | AMC | ENOC | 508 | FUJ | CHILLER 1-5 DOWN COVER SHEET DETACHED | VIGNESH | SELVAN | 12:55 | 13:30 | FIXED THE CHILLER DOWN COVER PROPERLY IT'S WORKING |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 21:25 | 120260486 |  | 0 | AMC | ENOC | 1634 | DXB | WALKIN CHILLER HIGH TEMP | MOHAMMED | MUTHUKUMAR | 23:00 | 1:20 | FOUND AND REST THE CONTROLLER AND CHECK THE SYSTEM GAS AND ELECTRICAL SIDE |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 11:16 | 120260487 | 120260250 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | BUTCHERY CHILLER HIGH TEMP | RANDOLPH | TROVEE | 13:35 | 3:10 | ICE FORMATION REMOVED AND REPLACED THE DEFECTIVE BOX FAN MOTOR | USED: AXIAL FAN 120*120-2NOS BY ONTEGRA |  | COMPLETED | WORK COMPLETED
2026-01-16 | 11:27 | 120260488 | 120260251 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | F&V CHILLER NOT WORKING | FROILAN |  | 16:40 | 17:00 | PLUGIN THE UNIT IN THE POWER SOCKET AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 12:50 | 120260489 | 120260252 | 1 | AMC | AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | OPEN CHILELR WATER LEAK | AHSAN |  | 14:30 | 17:00 | FIXED THE PIPE LINE BY REDUSER AND WATER LEAK ARRESTED |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 13:26 | 120260490 | 120260253 | 2 | AMC | AD COOP/DEYAAR | MBZ | AUH | BAKERY CHILLER NOT WORKING | RANDOLPH | TROVEE | 17:40 | 18:11 | DEFECTIVE CONDENSER FAN MOTOR, NEED REPLACE | NEED: COND FAN MOTOR 16-25W-1, ROUND ROCKER SWITCH-1 |  | COMPLETED | WORK COMPLETED | ON 17JAN26
2026-01-16 | 15:16 | 120260491 | 120260254 | 1 | AMC | AD COOP/DEYAAR | SPAR SAADIYAT | AUH | VEG CHILLER NOT WORKING | RANDOLPH | TROVEE | 15:40 | 16:36 | REMOVED THE ICE FORMATION AND CLEAN THE EVP |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 17:00 | 120260492 | 120260255 | 1 | AMC | AD COOP/DEYAAR | SE13 | AUH | CHEESE CHILLER DISPLAY WATER LEAK | OLIVER | FROILAN, WILLIAM | 17:10 | 18:07 | VACUUM THE WATER PAN AND DRAIN PIPE, DAMAGED PIPE IS OKAY FREE FLOW OF WATER |  |  | COMPLETED | WORK COMPLETED
2026-01-16 | 19:42 | 120260493 | 120260256 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER HAVE TOO MUCH ICE INSIDE | OLIVER | FROILAN, WILLIAM | 20:51 | 12:41 | CONDUCT LEAK TEST AND FOUND LEAK IN THE EXPANSION VALVE. REPLACED THE LIQUID LINE FILTER DRIER AND VACUUM THE EVP AND UNIT WORKING NORMAL | USED: R404A-2, FILTER DRIER164 1/2-1, SILFOS ROD-1 B Y DEYAAR |  | COMPLETED | WORK COMPLETED
2026-01-16 |  | 120260494 | 120260102 | 3 | AMC | ADNOC | 634 | SHJ | ICE MACHINE WATER LEAK | AHSAN |  | 18:15 | 19:45 | REPLACED THE WTAER FILTER AND CHECKED THE UNIT NOW OKAY | USED: WATER FILTER SET-1, 1/2*1/2 SOCKET-1, 1/2*3/4-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-16 | 14:40 | 120260495 | 120260238 | 2 | AMC | ADNOC | 596 | FUJ | FREEZER HIGH TEMP AND ITEMS ARE MELTING | VIGNESH | SELVAN | 14:40 | 18:00 | REPLACED THE NEW FILTER DRIER AND REPROCESS DONE | USED: FILTER DRIER 1/4 SOLDER-1, R404A-1, ORIFICE #0-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-16 |  | 120260496 | 120260203 | 3 | AMC | GRANDIOSE | AL SOYOUH | SHJ | INSTALLTION OF EVP FAN MOTOR AND PCB BOARD | DENNIS, ROGER | ROGER |  |  | REPLACED THE PCB BOARD AND EVP FAN MOTOR | NEED TO REPLACE COMPRESSOR DUE TO PUMPING ISSUE |  | COMPLETED | WORK COMPLETED
2026-01-16 |  | 120260497 | PPM | 37 | AMC | CAREEM | MARINA | DXB | PPM Q3 | SUDHEESH | ABIJITH |  |  | ALL UNIT SERVICE DONE WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-16 |  | 120260498 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 7:50 | 20:45 | SHJ ACCOMADATION PICK UP AND DROP IN CAREEM MARINA, DIERA MATERIAL PURCHASE, QAMAR AL HUDA MATERIAL COLLECTION TO WAREHOUSE DELIVERY AND TRANSPORT SHJ TEMA |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 8:21 | 120260499 | 120260257 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | RAW VEG CHILLER ICE FORMATION / READY TO EAT CHILLER HIGH TEMP | RANDOLPH | TROVEE | 9:30 | 11:08 | MANUALLY DEFROST THE ICE FORM THE EVP, RELOCATED THE DEFROST SENSOR AND ADJUST THE DEFROST SETTING / CHILLER ICE FORMATION REMOBVED AND MANUAL DEFROST THE SYSTEMA ND UNIT DEFROST SETTING CHANGED |  |  | ATTENDED
2026-01-17 | 11:51 | 120260500 | 120260258 | 1 | AMC | AD COOP/DEYAAR | ZAYED 1ST | AUH | BUTCHERY COLD ROOM STORAGE UNIT ICE FORMATION | RANDOLPH | TROVEE | 12:46 | 14:40 | DISMANTLE THE EVP FAN MOTOR & REMOVED THE ICE FORMATION AND DISPLAY CHILLER REMOVED THE ICE FORMATION AT EVP COIL |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 13:10 | 120260501 | 120260259 | 1 | AMC | AD COOP/DEYAAR | BAIN AL JESSRAIN | AUH | CHILLER TRIPPING ISSUE | OLIVER | FROILAN, WILLIAM | 13:48 | 15:01 | DISCONNECTED THE LED LIGHT OF EGG CHILLER , NEED TO REPLACE | NEED: LED LIGHT 5FT-1, OSRON LED LIGHT 2FT-1 |  | ATTENDED | NEED MATERIAL
2026-01-17 | 1:10 | 120260502 | 120260260 | 1 | AMC | AD COOP/DEYAAR | BAIN AL JESSRAIN | AUH | PROMOTIONAL CHILLER WATER LEAK | OLIVER | FROILAN, WILLIAM | 13:48 | 15:01 | REFILL THE SILCON ON THE GAP OF THE EVP AREA AND OKAY | USED: SILICON BY ONTRGRA |  | COMPLETED | WORK COMPLETED
2026-01-17 | 16:49 | 120260503 | 120260261 | 2 | AMC | AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE POWER TRIPPING | OLIVER | FROILAN, WILLIAM | 18:30 | 19:45 | FOUND GEAR MOTOR DEFECTIVE, NEED TO REPLACE | NEED: GEAR MOTOR-1NO |  | ATTENDED | ATTENDED ON 31?1?2026
2026-01-17 | 17:00 | 120260504 | 120260253 | 2 | AMC | AD COOP/DEYAAR | MBZ | AUH | BAKERY CHILLER NOT WORKING | OLIVER | FROILAN, WILLIAM | 17:00 | 17:53 | REPLACED THE DEFECTIVE CONDENSER FAN MOTOR AND ROCKER SWITCH, RESTARTED THE UNIT WORKING NORMAL | USED: COND FAN MOTOR 16-25W-1, ROUND ROCKER SWITCH-1 |  | COMPLETED | WORK COMPLETED
2026-01-17 | 9:11 | 120260505 | 120260262 | 1 | AMC | ANSAR | KARAMA | DXB | FREEZER WATER LEAK | SADAM |  | 18:00 | 19:05 | CLEANED THE PEPSI CHILLER DRAIN LINE NOW NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 9:35 | 120260506 | 120250263 | 1 | AMC | LULU | DIP | DXB | FREEZER COLD ROOM DEF SETTING NEED TO CHANGE / FREEZER NOISE ISSUE | SHAFI | MUSTAFA | 14:00 | 14:45 | EVP GRILL BROKEN, GRILL TOUCHED IN THE LEAD. REMOVDE THE BROKEN GRILL AND ADJUST THE DEFROST TIMING |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 12:28 | 120260507 | 120250264 | 1 | AMC | BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER HEADER NO COOLING | AHSAN | SELVAN | 13:30 | 18:50 | FILTER DRIER BLOCK. REPLACED FILTER DRIER AND REPROCESS DONE UNITB WORKING NORMAL | USED: 3/4 FILTER DRIER-1, SILVER ROD-1, R22 BY STORE |  | COMPLETED | WORK COMPLETED
2026-01-17 | 16:36 | 120260508 | 120260265 | 2 | AMC | CAREEM | UMS | DXB | ICE CREAM FREEZER HIGH TEMP | MOHAMMED | MUTHUKUMAR | 19:00 | 19:45 | FOUND COND FAN MTOOR DEFECTIVE, NEED TO REPLACE | NEED: TECUMSEH COMPRESSOR-1, R404A-1, FILTER DRIER 1/4 SOLDER-1, BLUE ROD-2, MITROGEN SAMLL-1, WULDING AND BLUE ROD-2, ACCESS VALVE-2NOS |  | COMPLETED | WORK COMPLETED | ON 19JAN26
2026-01-17 | 20:24 | 120260509 | 120260266 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | FREEZER ROCKER SWITCH DAMAGE | AHSAN | [6 empty] | COMPLETED
2026-01-17 | 22:24 | 120260510 | 120260267 | 1 | AMC | CAREEM | AL QUOZ | DXB | FREEZER COLD ROOM HIGH TEMP | MOHAMMED | MUSTAFA | 24:39 | 4:40 | EVP COIL SERVICE DONE AND ICE FORMATION REMOVED AND UNIT RESTARTED WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 9:12 | 120260511 |  | 0 | AMC | ENOC | 1127 | SHJ | OPEN CHILLER HIGH TEMP | AHSAN | SELVAN | 9:40 | 10:50 | NEED TO REPLACED THE CONTROLLER | NEED: EMERSON XCM25D-1NO |  | ATTENDED | NEED MATERIAL
2026-01-17 | 12:13 | 120260512 | 7100291986 | 1 | AMC | ENOC | 1080 | DXB | WATER Leaking under OPEN CHILLER | SADAM |  | 13:30 | 14:00 | FLOOR DRAIN LINE BLOCK, NEED TO CLEAR WITH PLUMBER |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 12:13 | 120260513 | 7100291988 | 3 | AMC | ENOC | 1085 | DXB | Walk in chiller plastic curtain is damag | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 18JAN26
2026-01-17 | 12:13 | 120260514 | 7100292003 | 2 | AMC | ENOC | 95 | DXB | OPEN CHILLER DOOR NO. 2 SHELVES RUSTY | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 19JAN26
2026-01-17 | 12:13 | 120260515 | 7100292007 | 2 | AMC | ENOC | 1009 | DXB | WALK IN FREEZER ICE FORMATION | SADAM | ZALAUDDIN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 19JAN26
2026-01-17 | 11:30 | 120260516 | 7100291867 | 2 | AMC | ENOC | 1088 | DXB | Walking freezer ice formation | SADAM |  | 11:30 | 12:30 | PVC CURTAIN DAMAGE AND NEED TO REPLACE | NEED: PVC CURTAIN 2MTR-3NOS, 5/8 INSULATION-1, BLACK TAPE-1, SILICON-1 |  | ATTENDED | NEED MATERIAL
2026-01-17 | 14:05 | 120260517 |  | 0 | AMC | ENOC | 66 | DXB | OPEN CHILLER NOT WORKING | SHAFI | MUSTAFA | 19:30 | 20:15 | REPLACED NEW CONTACTOR AND RESTART THE UNIT WORKING NORMAL | USED: CONTACTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-17 | 13:00 | 120260518 | 7100291961 | 2 | AMC | ENOC | ZOOM4009 | DXB | chiller 3 water leaking | SARAVANAN |  | 13:00 | 14:10 | REPLACED THE DEFECTIVE FLOAT SWITCH, WORKING NORMAL | USED: FLOT SWITCH 220V-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-17 | 12:30 | 120260519 |  | 0 | AMC | ENOC | 1127 | SHJ | OPEN CHILLER - CONTROLLER REPLACEMENT | VIGNESH |  | 12:30 | 14:10 | REPLACED THE CONTROLLER AND WORKING NORMAL | USED: COPELAND XCM25D-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-17 | 14:37 | 120260520 |  | 0 | AMC | ENOC | 1092 | DXB | OPEN CHILLER HIGH TEMP | MOHAMMED | MUTHUKUMAR | 20:20 | 22:50 | CONDENSER COIL WATER SERVICE, UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 15:25 | 120260521 | 5000216747 | 2 | AMC | ENOC | ZOOM4016 | DXB | OPEN CHILLER WATER LEAK | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED I18JAN26
2026-01-17 | 14:30 | 120260522 |  | 0 | AMC | ENOC | 1074 | DXB | WALKIN FREEZER 2 DOOR NOT COOLING AUTOMATICALLY. REPLACEMENT OF NEW SPRING TENSION SET, NEW GASKET WITH NEW PLASTIC HOLDER | DENNIS, SHAFI | MUSTAFA | 15:10 | 17:30 | REPLACED THE GLASS DOOR TENSION SET , GLASS DOOR GASKET HOLDER AND GASKET. UNIT CHECKED ALL WORKING NORMAL | USED: GLASS DOOR SPRING TENSION SET-2, GLASS DOOR GASKET HOLDER SET-2, GLASS DOOR GASKET-2 |  | COMPLETED | WORK COMPLETED
2026-01-17 | 16:15 | 120260523 | 7100289807 | 3 | AMC | ENOC | ZOOM4002 | DXB | WATER LEAK FROM CHILLER#3 | SARAVANAN |  | 16:15 | 18:45 | REPLACED THE HEATER AND SPARES, UNIT RETSARTED WORKING NORMAL | USED: DRAIN PAN HEATER 75CM-1, DRAIN PAN FLOAT SWITCH-1, MAG CONTACTOR 12AMPS-1 |  | COMPLETED | WORK COMPLETED
2026-01-17 | 19:40 | 120260524 | 7100291870 | 2 | AMC | ENOC | 1041 | DXB | Walk in chiller bulb light 4 nos. busted | SARAVANAN |  | 19:40 | 19:45 | NOT OUR SCOPE |  |  | ATTENDED | NOT OUR SCOPE
2026-01-17 | 21:45 | 120260525 | 7100291888 | 2 | AMC | ENOC | 1012 | DXB | Walk in chiller ceiling lights are buste | SARAVANAN |  | 21:45 | 22:00 | REPLACED THE DEFECTIVE LIGHT AND WORKING NORMAL | USED: 4FT LED TUBE LIGHT-2NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-17 |  | 120260526 | 7100291644 | 3 | AMC | ENOC | 1022 | DXB | FREEZER CURTAIN IS DAMAGED | MOHAMMED |  | 21:45 | 10:15 | NEED TO REPLACE PLASTIC CURTAIN | NEED: PLASTIC CURTAIN-4NOS (196CM) |  | ATTENDED | WORK CLOSE ON 28/1/26
2026-01-17 | 1:14 | 120260527 |  | 0 | AMC | ENOC | 1063 | DXB | BED FREEZER SHUTDOWN | MOHAMMED |  | 2:00 | 3:30 | BED FREEZER STARTED AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 7:55 | 120260528 | 120260268 | 1 | AMC | TCS | UMS | DXB | ICE CREAM FR5EEZER HIGH TEMP | SARAVANAN |  | 10:00 | 12:10 | REMOVED THE ICE FORMATION BY MANUAL DEFROST AND UNIT WORKING NORMAL | FREEZER#1, 2, 3 LEAK NEED TO CHECK |  | COMPLETED | WORK COMPLETED
2026-01-17 | 15:50 | 120260529 | 120260269 | 1 | AMC | TCS | EMERALD COURT | DXB | ICE MACHINE NOT WORKING | MOHAMMED | MUTHUKUMAR | 5:00 | 5:45 | REMOVED THE BLOCK AND CLEANED, APPLIES SILICON AND RESTARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 12:27 | 120260530 | 120260270 | 1 | AMC | NESTO | FUJAIRAH MALL | FUJ | FREEZER CABINET HIGH TEMP | SABITH ALI | BIJU, LORIMER | 20:10 | 23:40 | FREEZER 4, 6, 7, 8 , 9 UNITS ICE FORMATIOJ REMOVED AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 14:22 | 120260531 | 120260271 | 1 | AMC | NESTO | AL FAHIDI | DXB | SOFT DRINKS CHILLER WATER LEAK | SADAM |  | 15:50 | 17:30 | CLEAN THE DRAIN LINE AND CHECKED WITH WATER PASSAGE OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-17 | 15:39 | 120260532 | 120260272 | 1 | AMC | ADNOC | 794 | AUH | WALKIN FREEZER NOT WORKING | RANDOLPH | TROVEE | 16:00 | 16:30 | ICE REMOVED BY DEFROSTTING THE UNIT AND SET ANOTHER DEFROST |  |  | COMPLETED | WORK COMPLETED
2026-01-17 |  | 120260533 | MONTHLY REPORT | 4 | AMC | NESTO | AJF | AJM | MONTHLY REPORT | RACEL |  | 20:26 | 14:25 | FREEZER PIPE NEED TO REINSULATE, DELI SECTION EVP LEAKAGE FOR REPAIR, ISLAND FREEZERV ALL NIGHT CURTAIN NEED TO RRPLACE |  |  | COMPLETED | WORK COMPLETED
2026-01-17 |  | 120260534 | MONTHLY REPORT | 4 | AMC | NESTO | AJG | AJM | MONTHLY REPORT | RACEL |  | 11:00 | 24:30 | VISUAL INSPECTION FINDINGS |  |  | COMPLETED | WORK COMPLETED
2026-01-17 |  | 120260535 | MONTHLY REPORT | 4 | AMC | NESTO | AJE | AJM | MONTHLY REPORT | RACEL |  | 9:00 | 10:30 | VISUAL INSPECTION FINDINGS |  |  | COMPLETED | WORK COMPLETED
2026-01-17 |  | 120260536 | PPM | 37 | AMC | CAREEM | E& | AUH | PPM Q3 | OLIVER | FROILAN, WILLIAM |  |  | ALL UNIT WORKING NORMAL, LIGHT HAVE ISSUE |  |  | COMPLETED | WORK COMPLETED
2026-01-17 |  | 120260537 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  |  |  | SHJ ACCOMADATION PICK, CHOITHRAMS DROP AND ZOOM 1625, ENOC 1606 SHABAN SITE VISIT TRRANSOPORT |  |  | COMPLETED | WORK COMPLETED
2026-01-18 | 12:19 | 120260538 | 120260273 | 1 | AMC | AD COOP/DEYAAR | EMIRATES TOWER | AUH | BUTCHERY STORE TEMP HIGH | RANDOLPH | TROVEE | 1:00 | 1:55 | CLEANED THE CONDENSER COIL AND CHARGED THE REF AND CONDUCT LEAK TEST AND WORKING NORMAL | USED: R22 BY BRANCH |  | COMPLETED | WORK COMPLETED
2026-01-18 | 7:25 | 120260539 | 120260274 | 2 | AMC | NESTO | FUJAIRAH MALL | FUJ | FREEZER HIGH TEMP | RACEL | ROGER | 14:00 | 21:25 | CLEANED THE CABINETS AND FOUND DEFECTIVE EVP BOX FAN MOTOR, NEED TO REFPLACE. DRIPPING TIME SET TO 10MINS AND DEFROST TIME SET TO 20DEG/C | NEED: 120*120BOX FAN MOTOR-1NO |  | ATTENDED | NEED MATERIAL
2026-01-18 | 11:50 | 120260540 | 120260275 | 1 | AMC | NESTO | AL FAHIDI | DXB | BAKERY CHILLER ICE FORMATION
2026-01-18 | 19:39 | 120260541 | 120260276 | 1 | AMC | NESTO | KARAMA | DXB | COMBI FREEZER LIGHT NOT WORKING | MOHAMMED | MUTHUKUMAR | 22:00 | 23:30 | NEED TO REPLACE LIGHT | NEED: 3FT TUBE LIGHT-4NOS (TL-D 30W/840 |  | ATTENDED | NEED MATERIAL
2026-01-18 | 8:47 | 120260542 | 120260277 | 3 | AMC | LULU | MAQAM | AL AIN | CHEESE CHILLER LIGHT NOT WORKING | TALIB |  |  |  | ATTENEDED |  |  | ATTENDED | ATTENDED ON 19JAN26
2026-01-18 | 13:01 | 120260543 | 120260278 | 2 | AMC | ANSAR | KARAMA | DXB | FREEZER LIGHT NOT WORKING | AHSAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 20JAN26
2026-01-18 | 13:31 | 120260544 | 120260279 | 1 | AMC | BANIYAS COOP | SARAB | AUH | ISLAND FREEZER HIGH TEMP | RANDOLPH | TROVEE | 14:36 | 16:00 | TRANSFER REF GTOM CHILLER TO FREEZER |  |  | COMPLETED | WORK COMPLETED
2026-01-18 | 17:18 | 120260545 | 120260280 | 1 | AMC | BANYA FORREST | BLUE WATER | DXB | KITCHEN AC IS DOWN NOT WORKING | MOHAMMED | MUTHUKUMAR | 24:30 | 3:10 | FOUND ACCTUATOR VALVE DEFECTIVE, NOW TEMPORARY BY PASS AND CLEANED THE STAINER FILTER AND AIR FILTER. | NEED: DANFOSS ACCTUATOR VALVE CONTROL (AME 110 NL 082H8057)-1NO |  | ATTENDED | NEED MATERIAL
2026-01-18 | 18:14 | 120260546 | 120260281 | 2 | AMC | GRANDIOSE | AL SOYOUH | SHJ | WALKIN FREEZER HIGH TEMP | RACEL | ROGER | 22:18 | 23:00 | FOUND COMPRESSOR DEFECTIVE, NEED TO REPLACE | NEED: DANFOSS NTZ096A4LR1B COMPRESSOR-1, DANFOSS KVL1504-1, FILTYER DRIER 3/8 FLARE TYPE-1, R404A-1, NITROGEN-1, R141B-1 |  | ATTENDED | NEED MATERIAL
2026-01-18 | 20:05 | 120260547 | 120260282 | 2 | AMC | LULU | NUAIMIA | AJM | CHILLER TEMP AND ICE FORMATION ISSUE | RACEL |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 19JAN26
2026-01-18 | 20:08 | 120260548 | 120260283 | 1 | AMC | CAREEM | MARINA | DXB | OPEN CHILLER CHILLER TRIPPING ISSUE | MOHAMMED | MUTHUKUMAR | 20:10 | 21:15 | REMOVED THE BRAKER WIRE AND REFIXED. NEED TO REPLACE THE BREAKER IF AGAIN SAME TRIPPING ISSUE TAKES PLACE | NEED: CIRCUIT MAIN BREAKER (2P25AMPS)-1NO |  | ATTENDED | NEED MATERIAL
2026-01-18 | 11:30 | 120260549 | 7100291567 | 2 | AMC | ENOC | 2020 | DXB | BED FREEZER LIGHT NOT WORKING | SARAVANAN |  | 11:30 | 11:40 | CHECK THE BED FREEZER LIGHT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-18 | 12:30 | 120260550 | 5000216747 | 2 | AMC | ENOC | ZOOM4016 | DXB | OPEN CHILLER WATER LEAK | SARAVANAN |  | 12:30 | 13:00 | DRAIN BLOCK RECTIFIED, WATER LEAK ARRESTED AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-18 | 13:35 | 120260551 | 7100291941 | 2 | AMC | ENOC | 1056 | DXB | vertical freezer 1 light busted | SARAVANAN |  | 13:35 | 13:45 | LIGHT HOLDER LOSE CONNECTION RECTIFIED, NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-18 | 16:00 | 120260552 | 7100291988 | 3 | AMC | ENOC | 1085 | DXB | Walk in chiller plastic curtain is damag | SARAVANAN |  | 16:00 | 16:50 | NEED TO REPLACE CURTAIN | NEED: PLASTIC CURTAIN 2MTRS-6NOS |  | ATTENDED | NEED MATERIAL
2026-01-19 | 8:27 | 120260553 | 120260284 | 1 | AMC | STELLAR OCEAN | AL QUOZ | DXB | FREEZER COLD ROOM NOT WORKING | SARAVANAN |  | 10:15 | 11:30 | TRIP OFF THE BREAKER, RESTARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 9:10 | 120260554 | 120260285 | 1 | AMC | BAQER MOHEBI | ABU HAIL | DXB | CHEESE AND MILK CHILLER WATER LEAK AND LIGHT NOT WORKING | AHSAN |  | 13:00 | 13:45 | WATER LEAK PROBLEM FOR MAIN DRAIN LINE BLOCK, NEED TO CLEAR THIS ISUSE |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 9:17 | 120260555 | 120260286 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | CHILLER LIGHT NOT WORKING | AHSAN |  | 9:30 | 17:22 | REPLACED THE TIMER DELAY, PHASE FAILURE, ROCKER SWITCH | USED: TIMER DELAY-1, PHASE FAILURE-1, ROCKER SWITCH-1 |  | COMPLETED | WORK COMPLETED
2026-01-19 | 9:36 | 120260556 | 120260287 | 1 | AMC | LULU | AL RAFFA | DXB | COLD ROOM LIGHT NOT WORKING | SADAM | ZALAUDDIN | 10:26 | 11:15 | REPLACED THE NEW LED LIHGHT | USED: LED T8 2FT TUBE-2 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-19 | 9:30 | 120260557 | 120260277 | 3 | AMC | LULU | MAQAM | AL AIN | CHEESE CHILLER LIGHT NOT WORKING | TALIB |  | 9:30 | 10:35 | REPAIR THE LIGHTWORKING NORMAL AND REMOVED FOR REPAIR | NEED: LED LIGHT-1NO (NEED TO REPAIR) |  | COMPLETED | WORK COMPLETED | ON 21JAN26
2026-01-19 | 11:33 | 120260558 | 120260288 | 1 | AMC | WESTLAND | AL AIN | AL AIN | OLD UNIT NOT WORKING PROPERLY | TALIB |  | 13:20 | 18:05 | WATER WASH EVP COIL AND CLEAR AND START THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 8:00 | 120260559 | 120260282 | 2 | AMC | LULU | NUAIMIA | AJM | CHILLER#1 & #2 TEMP AND ICE FORMATION ISSUE | RACEL |  | 8:44 | 11:55 | CLEANED THE EVP COIL AND REMOBVED THE ICE FORMATION. RESTARTED THE UNIT AND WORKING NORMAL / REMOVED THE REF AND REPROCESS THE SYATEM AND VACUUM THE SYSTEM AND RESTARTED THE UNIT | USED: 0.90KG |  | COMPLETED | WORK COMPLETED
2026-01-19 | 8:00 | 120260560 | 120260289 | 1 | AMC | LULU | NUAIMIA | AJM | VEG COLD ROOM CHILLER WTAER LEAK | RACEL |  | 8:44 | 11:55 | REMOVE THE WATER FROM THE DRAIN PAN AND CLENAED THE TRAY AND NO WATER LEAK |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 12:59 | 120260561 | 120260265 | 2 | AMC | CAREEM | UMS | DXB | ICE CREAM FREEZER HIGH TEMP | SADAM | ZALAUDDIN | 13:45 | 18:40 | REMOVE THE OLD COMPRESSOR AND FIXED NEW COMPRESSOR, FILTER DRIER AND REPROCESS DONE | USED: TECUMSEH COMPRESSOR-1, R404A-1, FILTER DRIER 1/4 SOLDER-1, BLUE ROD-2, MITROGEN SAMLL-1, WULDING AND BLUE ROD-2, ACCESS VALVE-2NOS |  | COMPLETED | WORK COMPLETED
2026-01-19 | 16:56 | 120260562 | 120260290 | 1 | AMC | CAREEM | CITYLAND | DXB | COLD ROOM DOOR LOCK INSIDE CAP MISSING | MOHAMMED | MUTHUKUMAR | 20:20 | 20:55 | NOW TEMPORARY FIXE THE MISSING CAP |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 14:30 | 120260563 | 120260291 | 2 | AMC | GRANDIOSE | HOOR 17 | DXB | CDU ISTALLATION FOR RECEIVING AREA | SHAFI, SABITH, SARAVANAN | BIJU, LORIMER, WILSON, MUSTAFA | 16:30 | 24:00 | POSTIONED THE SYSTEMA AND FIXED THE PIPE AND FLUSH WITH NITRIGEN AND DONE LITTLE PIPING | NEED MATERIAL TO CONTINUE THE JOB |  | COMPLETED | WORK COMPLETED | ON 20JAN26
2026-01-19 | 9:41 | 120260564 | 7100292404 | 1 | AMC | ENOC | 1142 | SHJ | WALKIN FREEZER WATER LEKA AND ICE FORMATION | VIGNESH | SELVAN | 18:20 | 19:00 | NEED SCHEUDLE FOR SHUTDOWN AND SIDE DRAINAGE TRAY FULL DAMAGE |  |  | ATTENDED | NEED SCHEDULE
2026-01-19 | 9:30 | 120260565 | 7100292007 | 2 | AMC | ENOC | 1009 | DXB | WALK IN FREEZER ICE FORMATION | SADAM | ZALAUDDIN | 9:30 | 10:00 | DOOR GASKET DAMAGE NEED TO REPLACE | NEED: DOOE GASKET-1 (97CM*193CM) |  | ATTENDED | NEED MATERIAL
2026-01-19 | 11:55 | 120260566 | 7100292003 | 2 | AMC | ENOC | 95 | DXB | OPEN CHILLER DOOR NO. 2 SHELVES RUSTY | SARAVANAN |  | 12:45 | 13:00 | BOTTOM GASKET PLATE RUSTY AND NEED TO POWDER QUOTE (WHITE) | NEED: LEN-135CM, H-190CM |  | ATTENDED | NEED MATERIAL
2026-01-19 | 12:45 | 120260567 | 7100292205 | 2 | AMC | ENOC | 1023 | DXB | Bed-freezer lights not working. | SADAM | ZALUDDIN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 20JAN26
2026-01-19 | 12:45 | 120260568 | 7100292222 | 1 | AMC | ENOC | 1079 | DXB | Bed freezer top glass | SHABAN |  |  |  | UNDER SHABAN |  |  | NOT ATTENDED | UNDER SHABAN
2026-01-19 | 12:45 | 120260569 | 7100292223 | 1 | AMC | ENOC | 1081 | DXB | pronto display chiller not working | SARAVANAN |  | 13:35 | 13:40 | NOT UNDER OUR SCOPE |  |  | ATTENDED | NOT OUR SCOPE
2026-01-19 | 12:45 | 120260570 | 7100292284 | 2 | AMC | ENOC | 1007 | DXB | CHILLER LIGHT | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 21JAN26
2026-01-19 | 12:45 | 120260571 | 7100292299 | 2 | AMC | ENOC | 1079 | DXB | DELI CHILLER 1 BLOCKED DRAINAGE | SADAM | ZALAUDDIN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 20JAN26
2026-01-19 | 12:45 | 120260572 | 7100292304 | 2 | AMC | ENOC | 1099 | DXB | Vertical Chiller for Flower | SARAVANAN |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 21JAN26
2026-01-19 | 12:45 | 120260573 | 7100292327 | 1 | AMC | ENOC | 1005 | DXB | walk-in chiller temperature not stable. | SARAVANAN |  | 14:00 | 15:30 | COMPRESSOR FAN MOTOR ALL WORKING NORMAL AND ADJUST THE DEFROST SETTING |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 8:14 | 120260574 | 120260292 | 1 | AMC | NESTO | AJE | AJM | VEG CHILLER HIGH TEMP | RACEL |  | 12:16 | 13:25 | TRACE THE ISSUE OF ELECTRICAL POWER. THIS CIRCUIT BREAKERCONNECTED SUPPLY FOR AC. NOW RESET THE BREAKER AND THAT NOT OUR SIDE ISSUE |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 10:18 | 120260575 | 120260274 | 2 | AMC | NESTO | FUJAIRAH MALL | FUJ | ISLAND FREEZER MOISTURE ISSUE | RACEL |  | 16:02 | 17:01 | REPLACED THE EVP BOX FAN MOTOR AND RESTARTED THE UNIT WORKING NORMAL | USED: BOX FAN MOTOR 120*120-1NO |  | COMPLETED | WORK COMPLETED
2026-01-19 | 12:56 | 120260576 | 120260294 | 1 | AMC | NESTO | AL AIN CENTER | AL AIN | BUTCHERY CHILLER FAN NOT WORKING | TALIB |  | 24:00 | 3:05 | FULL WATER SERVICE AND CLEAR THE ICE AND DRAIN LINE CLEANED AND RESTARTED THE UNIT CHECKED ALL NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 13:57 | 120260577 | 120260295 | 1 | AMC | NESTO | AJE | AJM | CHILLER ICE FORMATION | VIGNESH | SELVAN | 21:50 | 22:40 | CHECKED THE OPEN CHILLER IT IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 14:30 | 120260578 | 120260296 | 1 | AMC | NESTO | MAYSALOON | SHJ | FISH COLD ROOM LIGHT NOT WORKING | VIGNESH | SELVAN | 20:25 | 21:20 | DOOR LOCK DAMAGE NEED TO REPLACE AND EVP UNIT SAFETY COVER DAMAGE / FISH COLD ROOM LIGHT IS WORKING NORMAL | NEED: EVP FAN MOTOR SAFETY COVER-4NOS, DOOR LOCK FULL SET-1NO |  | ATTENDED | NEED MATERIAL
2026-01-19 | 15:56 | 120260579 | 120260297 | 1 | AMC | TCS | UMS | DXB | PORK FREEZER DIGITAL DISPLAY DAMAGE | MOHAMMED | MUTHUKUMAR | 21:30 | 21:45 | FOUND DISPLAY THERMOMETER DEFECTIVE, NEED TO REPLACE | NEED: DISPLAY THERMOMETER-1NO |  | ATTENDED | NEED MATERIAL
2026-01-19 | 18:25 | 120260580 | 120260298 | 1 | AMC | TCS | ROVE CITY CENTER | DXB | FREEZER LIGHT NOT WORKING / CHILELR WTAER LEAK | MOHAMMED | MUTHUKUMAR | 22:30 | 24:20 | DRAIN LINE BLOCK REMOVED / NEED TO CHECK THE LED DRIVE AND NEED TO SCHEDULE |  |  | ATTENDED | NEED SCHEDULE
2026-01-19 | 8:41 | 120260581 | 120260299 | 1 | AMC | AD COOP/DEYAAR | MADINAT ZAYED | AUH | DISPLAY CHILLER WATER LEAK | RANDOLPH | TROVEE, OLIVER | 8:30 | 9:21 | FLISHED THE DRAIN OF THE CABINET UNITIL THE BLOCK CLEAR AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 9:05 | 120260582 | 120260300 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | FREEZER#2 HIGH IN RECEIVING AREA 2 | RANDOLPH | TROVEE, OLIVER | 9:35 | 10:06 | DUE TO LOOSE CONNECTION IN COMPRESSOR CONTROLLER, TIGHTEN AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 9:05 | 120260583 | 120260301 | 1 | AMC | AD COOP/DEYAAR | AD MALL | AUH | CHILLER NOT COOLING | RANDOLPH | TROVEE | 10:30 | 11:15 | SWITCHED OF THE 2 CABINETS AND CLEANED THE CONDENSER FINS. AND RESTARTED THE UNIT NORMAL OPERATION |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 10:10 | 120260584 | 120260302 | 1 | AMC | AD COOP/DEYAAR | AL ZAHIYA | AUH | CHILLER NOISE ISSUE | OLIVER |  | 10:34 | 11:20 | REPLACED THE DEFECTIVE FAN MOTOR AND UNIT WORKING NORMAL | USED: FAN MOOTR 10-20W-2NOS |  | COMPLETED | WORK COMPLETED
2026-01-19 | 13:25 | 120260585 | 120260303 | 1 | AMC | AD COOP/DEYAAR | MUROOR | AUH | ICE MACHINE WATER LEAK | RANDOLPH | TROVEE, OLIVER | 14:11 | 14:32 | FIX THE DRAIN HOSE OF ICE MACHINE AND START THE UNIT AND CHECK OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 14:29 | 120260586 | 120260304 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | COLD ROOM EVP UNIT ICE FORMATION | RANDOLPH | TROVEE, OLIVER | 15:00 | 15:47 | REMOVED AND CLEANED THE ICE FORMATION | NEED: COLD ROOM DOOR RIGHT OPENING (98CM*193CM) DOOR FRAME, DOOR HEATER-6MTR, SILICON WHITE-5NOS |  | ATTENDED | NEED MATERIAL
2026-01-19 | 16:12 | 120260587 | 120260305 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | BUTCHERY CHILLER ICE FORMATION ISSUE | RANDOLPH | TROVEE, OLIVER | 16:45 | 17:00 | ADJUST THE SET POINT TEMP AT THE CONTROLLER OF BAKERY CHILLER OLAY |  |  | COMPLETED | WORK COMPLETED
2026-01-19 | 18:17 | 120260588 | 120260306 | 1 | AMC | AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | F&V STORE CHILLER WATER LEAK
2026-01-19 | 21:42 | 120260589 | 120260307 | 1 | AMC | AD COOP/DEYAAR | EMIRATES TOWER | AUH | FREEZER NOT WORKING AND SIDE MATERIAL MELTED | RANDOLPH | TROVEE | 22:20 | 23:35 | COMPRESSOR FOUND DEFECTIVE | NEED: COMPRESSOR-1, NITROGEN-1, FILTER DRIER 1/4-1, BLUE ROD-2, SILFOS ROD-2, ACCESS VALVE-2, R290-1CYL |  | ATTENDED | NEED MATERIAL
2026-01-19 | 7:45 | 120260590 | MINA PROJECT | 9 | AMC | AD COOP/DEYAAR | MINA | AUH | MINA INDULLATION REPLACEMNET WORK | DENNIS, ROGER | GOVIND, SUDHEESH, ABIJITH |  |  | SHUTDOWN THE UNIT AND INSULATION STARTED TO REMOVE |  |  | COMPLETED | WORK COMPLETED
2026-01-19 |  | 120260591 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 8:15 | 8:15 | AL BAZ MATERIAL COLLECTION NOT DONE, NAASER AL ZAHER COMPRESSOR COLLECTION AND DELIVERY TO SADAM, RASHIDIYA MATERIAL COLLECTION AND AMPEX MATERIAL COLLECTION AND DELIVER IN GRANDIOSE JADHAF |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 9:10 | 120260592 | 120260308 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | 2 FREEZERS ARE NOT WORKING | RANDOLPH | TROVEE | 18:43 | 19:30 | RESTARTED THE BREAKER AND UNIT WORKING NROMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 9:10 | 120260593 | 120260309 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | COMBI FREEZER NOT COOLING | RANDOLPH | TROVEE | 14:00 | 14:20 | ITEMS BLOCK THE AIR FLOW OF CABINET, REMOVED THE ITEMS AND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 9:49 | 120260594 | 120260310 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | F&V CHILLER IS NOT WORKING | RANDOLPH | TROVEE | 18:43 | 19:30 | FOUND DRAIN HEATER DEFECTIVE AND DISCONNECTED AND REPLACED, RESTART THE UNIT | USED: DRAIN HEATER-1 |  | COMPLETED | WORK COMPLETED
2026-01-20 | 9:51 | 120260595 | 120260311 | 1 | AMC | AD COOP/DEYAAR | AD MALL | AUH | TABLE TOP CHILLER NOT WORKING | OLIVER | FROILAN, WILLIAM | 13:21 | 14:21 | FOUND COMPRESSOR STUCK UP AND DEFECTIVE, NEED TO REPLACE | NEED: COMPRESSOR GL80TB-1, FILTER DRIER 1/4 SOLDER-1, R134A-1, R141B-1, MITROGEN-1, COPPER AND BLUE ROD-2, ACCESS VALVE-1 |  | ATTENDED | NEED MATERIAL
2026-01-20 | 14:42 | 120260596 | 120260312 | 1 | AMC | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | DOUBLE DOOR VERTICAL CHILLER HIGH TEMP | VIGNESH | SELVAN | 18:00 | 19:10 | FOUND ICE FORMATION IN THE VP COIL, REMOVED THE ICE AND RESTARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 9:08 | 120260597 | 120260313 | 1 | AMC | ANSAR | KARAMA | DXB | ALL CHILLER SHUTDOWN | AHSAN |  | 10:30 | 13:30 | FREEZER LIGHTS NEED TO REPLACE | NEED: T8 58CM LED LIGHT-17NOS, T8 90CM LED LIGHT-3NOS, T8 4FT LED LIGHT-2NOS |  | ATTENDED | NEED MATERIAL
2026-01-20 | 8:20 | 120260598 | 120260314 | 1 | WTY | CAREEM | SHAMKHA | AUH | COLD ROOM NOT WORKING | RANDOLPH | TROVEE, OLIVER | 10:00 | 12:01 | BREAK OF AC HAVE FAULT AND OUT DOOR UNIT TEMPORARY SWITCH OFF BREAKER OF AC AND TURN ON BREAKER, STARTE THE CHILLER AND FREEZER UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 11:13 | 120260599 | 120260315 | 3 | AMC | WESTLAND | AL AIN | AL AIN | OUTDOOR UNIT ACCUMULATOR ICE FORMATION / PREPARATION ROOM LOW COOLING | TALIB |  | 15:10 | 21:45 | REMOVED THE ICE FORMATION AND REDUSE THE PRESSURE 5PSI / UNIT CONDENSER COIL HAVE MULTIPLE LEAK AND NEED TO REPLACE | NEED CONDENSER COIL TO REPLACE |  | ATTENDED | NEED MATERIAL
2026-01-20 | 13:18 | 120260600 | 120260316 | 1 | AMC | BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER NOT WORKING | RACEL | AHSAN | 15:31 | 19:25 | REMOVE THE ITEM AND DEEP CLEAN THE EVP COIL AND HEATER ALL WORKING |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 13:28 | 120260601 | 120260317 | 2 | AMC | LULU | DIP | DXB | FREEZER COLD ROOM HIGH TEMP | MOHAMMED | MUTHUKUMAR | 12:00 | 14:50 | FREEZER CABINET#13 LIQUID LINE DOWN SIDE LEAK, FREEZER COLD ROOM ON EVP COIL BIG LEAK CAN’T SEE AND INSIDE COIL ALSO. NEED TO REPLACE TEMPORARY CLOSE THE VALVE | NEED: R404A-3CYL, 3/8 FILTER DRIER-1, EVP COIL MODEL (F45HC1306E7 CODE: 10054881)-1 |  | ATTENDED | NEED MATERIAL
2026-01-20 | 11:13 | 120260602 | 120260278 | 2 | AMC | ANSAR | KARAMA | DXB | FREEZER LIGHT NOT WORKING | AHSAN |  | 10:30 | 13:30 | CHECK THE PHASE VOLTAGE AND CONNECT DUCT AND START THE UNIT OKAY, REMOVED DAMAGE FAN MOTOR CONNECTION AND START THE COMPRESSOR | NEED: PHASE MONITORING DEVICE IL9077-1NO, COMPRESSOR COOLING FAN (S4E300-AP26-02/C01)-4NOS |  | ATTENDED | NEED MATERIAL
2026-01-20 | 16:14 | 120260603 | 120260318 | 1 | AMC | ADASI | ABU DHABI | AUH | FREEZER COLD ROOM NOT COOLING | RANDOLPH | TROVEE | 16:14 | 17:30 | SENSOR LOOSE CONNECTION AND TEIGHTEN |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 19:27 | 120260604 | 120260319 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | LEAF CHILLER TEMP ISSUE | VIGNESH | SELVAN | 21:30 | 2:50 | PRIMARY COIL LEAK ARRETSED AND VACUUM THE UNIT, CHARGED THE REF | USED: R404A BY STORE |  | COMPLETED | WORK COMPLETED
2026-01-20 | 15:31 | 120260605 | 120260247 | 2 | AMC | BAQER MOHEBI | ABU HAIL | DXB | CDU#6 FAN MOTOR NOT WORKING | RACEL |  | 15:30 | 19:30 | REPLACED THE COND FAN MOTOR | USED: 500MM, 220V-1NO |  | COMPLETED | WORK COMPLETED
2026-01-20 | 10:15 | 120260606 | 120260291 | 2 | AMC | GRANDIOSE | HOOR 17 | DXB | CDU ISTALLATION FOR RECEIVING AREA | DENNIS, SHAFI, SABITH | BIJU, MUSTAFA | 10:15 | 19:45 | REPLACED THE CDU UNIT, PIPE ALTERNATION DONE AND CONTROL PANEL FIXED, VIBNTATION ELIMINATOR FIXED, SIDE GLASS AND LEAK CHECK DONE.VACUMM AND CHARGED THE REF | USED: CDU UNIT-1, CONTROL PANEL-1, FILTER DRIRE-1, SIDE GLASS-1, SHUT OFF VALVE-1, COPPER PIPE-1, VIBRATION ELIMINATOR-1, U BEND-1, PIPE FITTINGS AND INSULATION, R404A-2 |  | COMPLETED | WORK COMPLETED
2026-01-20 | 21:12 | 120260607 | 120260320 | 2 | WTY | CAREEM | JVT | DXB | UNIT SERVICE | SADAM | ZALAUDDIN |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 21JAN26
2026-01-20 | 22:31 | 120260608 | 120260321 | 2 | AMC | BANIYAS COOP | SARAB | AUH | CAKE CHILLER TEMP ISSUE | RANDOLPH | TROVEE |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 21JAN26
2026-01-20 | 9:10 | 120260609 | 7100292299 | 2 | AMC | ENOC | 1079 | DXB | DELI CHILLER 1 BLOCKED DRAINAGE | SADAM | ZALAUDDIN | 9:10 | 10:00 | CLEAN THE DRAIN BLOCK, NOE WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 10:16 | 120260610 | 7100292485 | 1 | AMC | ENOC | 95 | DXB | Bed freezer 04 tripping | SADAM | ZALAUDDIN | 12:45 | 12:55 | UNIT NOT UNDER OUR SCOPE |  |  | ATTENDED | NOT OUR SCOPE
2026-01-20 | 10:16 | 120260611 | 7100292517 | 2 | AMC | ENOC | 1035 | DXB | WALK-IN CHILLER DOOR NOT CLOSING | SHAFI | MUSTAFA |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 22JAN26
2026-01-20 | 10:16 | 120260612 | 7100292579 | 3 | AMC | ENOC | ZOOM4009 | DXB | All chiller are leaking | SABITH ALI |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 22 JAN 2026
2026-01-20 | 10:16 | 120260613 | 7100292606 | 1 | AMC | ENOC | 1204 | AJM | tube Light Inside Freezer Not working | RACEL |  | 12:19 | 13:04 | RECTIFY THE CONNECTOR AND REFIX IT PROPERLY AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 13:20 | 120260614 |  | 0 | AMC | ENOC | 1055 | DXB | PRONTO AMBIENT DISPLAY CHILLER NOT WORKING | MOHAMMED | MUTHUKUMAR | 23:05 | 23:50 | UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED | UNIT NOT OUR SCOPE
2026-01-20 | 13:30 | 120260615 | 7100292205 | 2 | AMC | ENOC | 1023 | DXB | Bed-freezer lights not working. | SADAM | ZALUDDIN | 13:30 | 14:00 | SWITCH IS IN OFF CONDITION, WE SWITCH ON THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 7:14 | 120260616 | 120260322 | 1 | AMC | NESTO | AJE | AJM | CHILLER TEMP NORMAL BUT NO COOLING | RACEL |  | 8:35 | 11:50 | REMOVED THE ITYEMS AND CLEAN THE WHOLE CABINET EVP. REFIX THE EVP COVER AND ADJUSTED THE REF. RESTARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 9:01 | 120260617 | 120260323 | 1 | AMC | NESTO | ARJAN | DXB | OPEN CHILLER HIGH TEMP | SADAM | ZALAUDDIN | 10:30 | 12:00 | REPLACED THE DEFECTIVE FAN MOTOR AND UNIT WORKING NORMAL | USED: 16W FAN MOTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-20 | 22:02 | 120260618 | 120260324 | 2 | AMC | NESTO | AJF | AJM | BUTCHERY STEEL BODY CHILLER DOOR ISSUE | RACEL |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 21JAN26
2026-01-20 | 8:40 | 120260619 | 120260325 | 1 | AMC | TCS | UMS | DXB | FREEZER WATER LEAK | MOHAMMED | MUTHUKUMAR | 20:00 | 22:30 | TEMPORARY REMOVED THE ICE FORMATION AND FOUND DRAIN HETAER DEFECTIVE. AND PIPE NEED TO REPLACE | NEED: DRAIN HEATER 220V-2MTR, PV CPIPE 1"-2MTR, PVC ELBOW 1"-2NOS, PVC REDUSER 1"-3/4"-1NO, FOAM TAPE-1NO |  | ATTENDED | NEED MATERIAL
2026-01-20 | 14:20 | 120260620 | 120260326 | 1 | AMC | TCS | DARWISH HAMDAN | AUH | FREEZER UNIT ICE FORMATION | OLIVER | FROILAN | 15:01 | 17:00 | REMOVED THE ICE FORMATION AND RESTARTED THE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-20 | 20:00 | 120260621 | 120260327 | 2 | AMC | TCS | UMS | DXB | VEG & FRUIT CHILLER NOT WORKING | MOHAMMED | MUTHUKUMAR | 20:00 | 22:30 | FOUND CONDENSER FAN MOTOR DEFECTIVE, NEED TO REPLACE | NEED: CONDENSER FAN MOTOR (B042-4DK.24.6P) 3PH 440V-1NO |  | ATTENDED | ATTENDED ON 22/1/2026
2026-01-20 | 20:00 | 120260622 | MINA PROJECT | 9 | AMC | AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | ROGER | GOVIND, SUDHEESH, ABIJITH | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-20 |  | 120260623 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 9:10 | 20:15 | DIERA MATERIAL COLLECTION AND WARE HOUSE MATERIAL COLLECTION DROP IN GRANDIOSE HOOR 17, BAQER MOHEBI ABU HAIL MATYERIAL DELIVERY, AD COOP MUTEENA TRANSPORT |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 8:29 | 120260624 | 120260320 | 2 | WTY | CAREEM | JVT | DXB | UNIT SERVICE | SADAM | ZALAUDDIN | 9:30 | 11:00 | CLEAN THE CHILLER & FREEZER CDU CONDENSER COIL. CLEAN WITH PRESSURE WASHER AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 9:40 | 120260625 | FM2026086 | 1 | WTY | CAREEM | AL WASAL | DXB | COLD ROOM UNIT MOISTURE ISSUE | SADAM | ZALAUDDIN | 12:30 | 13:35 | NEED TO INSTALL PV CURTAIN | NEED: PVC CURTAIN 2MTR-1NO |  | ATTENDED | NEED MATERIAL
2026-01-21 | 11:01 | 120260626 | 120260329 | 1 | AMC | BANIYAS COOP | BANIYAS CENTER | AUH | EGG CHILLER PLEASE CHECK (FUNGUS / RUSTED) | RANDOLPH | TROVEE | 11:40 | 12:20 | WEEKLY THE STORE SHELVES WILL BE CLEANED |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 9:10 | 120260627 | 120260321 | 2 | AMC | BANIYAS COOP | SARAB | AUH | CAKE CHILLER TEMP ISSUE | RANDOLPH | TROVEE | 9:10 | 9:50 | REMOVED THE FILTER OF CONDENSER AND CLEAN THEN RETURN. START THE CHILLER AND OBSERVE THE OPERATION OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 13:30 | 120260628 | 120260277 | 3 | AMC | LULU | MAQAM | AL AIN | CHEESE CHILLER LIGHT NOT WORKING | TALIB |  | 13:30 | 14:40 | REPAIRED THE LIGHT AND FIXED | USED: LED LIGHT-1NO (REPAIRED) |  | COMPLETED | WORK COMPLETED
2026-01-21 | 9:45 | 120260629 | 120260330 | 3 | AMC | NADEC | SHARJAH | SHJ | LOADING AREA CHILLE#2 NOT WORKING | SABITH ALI | BIJU | 10:45 | 17:30 | CHECKED THE COMPRESSOR DEFECTIVE, NEED TO REPLACE | NEED: COMPRESSOR BITZER (4DC 7.2 40S)-1, R22-1, FILTER DRIER FLARE TYPE 1/2-1, CONTACTOR 25AMOS-1, OVERLOAD 18-22-1 |  | ATTENDED | NEED MATERIAL
2026-01-21 | 9:45 | 120260630 | 120260330 | 3 | AMC | NADEC | SHARJAH | SHJ | CHILLER COLD ROOM #2 EVP#1 & EVP#2 NOT COOLING | SABITH ALI | BIJU | 10:45 | 17:30 | EVP#1 CONDENSER FAN MOTOR NOT WORKING AND COMP NOT WORKING DUE TO LOW REF / EVP#2 COMPRESSOR ISSUE DUE TO MOTOR PROTECTION DAMAGE, NEED TO REPLACE AND LOW GAS IN SYSTEM | NEEd: COND FAN (YWF 4E 450SC)-1, MOTOR PROTECTION SE-B1 BITZER-1, R22-1 |  | ATTENDED | NEED MATERIAL
2026-01-21 | 9:45 | 120260631 | 120260330 | 3 | AMC | NADEC | SHARJAH | SHJ | COLD ROOM#1 TEMP ISSUE | SABITH ALI | BIJU | 10:45 | 17:30 | EVP#1 WORKING NORMAL / EVP#2 ELECTRICAL ISSUES AND 1 FAN MOTOR NOT WORKING, ELECTRICAL ISSUE CLEARED AND NEED TO REPLACE 1 PC EVP COIL FAN MTOOR. 2 UNIT OUT DOORS WORKING NORMAL | NEED: EVP COIL FAN MOTOR-1 (S4E400-AR01-62) 220V |  | ATTENDED | NEED MATERIAL
2026-01-21 | 9:45 | 120260632 | 120260331 | 1 | AMC | NADEC | SHARJAH | SHJ | LOADING AREA#1 CHILLER NOT WORKING | SABITH ALI | BIJU | 10:45 | 17:30 | OUTDOOR UNIT RIPPED AND FOUND CONDENSER FAN MOTOR NOT WORKING, NEED TO REPLACE | NEED: CONDENSER FAN MOTOR (S3G450-LL03 H7)-2NOS |  | ATTENDED | NEED MATERIAL
2026-01-21 | 10:30 | 120260633 | 120260281 | 2 | AMC | GRANDIOSE | AL SOYOUH | SHJ | COMPRESSOR REPLACEMNET FOR MONO BLOCK | DENNIS | RACEL | 11:31 | 5:30 | dismantled evp and flush 141b, replaced capilary tube and reinstall evp and replaced the defective compressor. Install new compressor and vacuum the system and ref charged | VARIOUS MATERIAL USED |  | COMPLETED | WORK COMPLETED
2026-01-21 | 7:37 | 120260634 | 120260332 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | FREEZER#2 HIGH TEMP | OLIVER |  | 8:35 | 9:05 | SENSOR DEFECTIVE, USED DEFROST SENSOR AND ADJUST THE DEFROST SETTING AND OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 8:32 | 120260635 | 120260333 | 1 | AMC | AD COOP/DEYAAR | MUROOR | AUH | CHILLER NOT COOLING | RANDOLPH | TROVEE | 10:14 | 10:38 | COMPRESSOR DEFECTIVE | NEED: EMBRACO COMPRESSOR (NEU6215GK)-1, FILTER DRIER SOLDER 1/4-1, SINGLE POLE MAG CONTACTOR 25A-1, R404A-1, R141B-1, NITROGEN-1, CHARGING PIN-2, SILFOS ROD-4NOS |  | ATTENDED | NEED MATERIAL
2026-01-21 | 9:53 | 120260636 | 120260334 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | CHILLER NOT WORKING | RANDOLPH | TROVEE | 11:00 | 11:17 | CHILLER FOUND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 15:27 | 120260637 | 120260335 | 1 | AMC | AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | F&V CHILLER WATER LEAK | RANDOLPH | TROVEE, OLIVER | 16:20 | 17:05 | FLUSHED THE DRAIN LINE AND OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 15:10 | 120260638 | 120260336 | 1 | AMC | AD COOP/DEYAAR | AD MALL | AUH | BEVERAGE CHILLER WATER LEAK | RANDOLPH | TROVEE, OLIVER | 15:10 | 16:00 | CLEANED THE DRAIN BLOCK AND WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 17:46 | 120260639 | 120260337 | 2 | AMC | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | PLUGIN CHILLER TRIPPING ISSUE | VIGNESH | SELVAN | 18:20 | 19:30 | DEFECTIVE FAN MOTOR AND NEED TO REPLACE | NEED: FAN MOTOR 5W-2, 16W FAN MOTOR-1 |  | ATTENDED | NEED MATERIAL
2026-01-21 | 9:43 | 120260640 | 120260338 | 1 | AMC | NESTO | FUJAIRAH MALL | FUJ | ISLAND FREEZER NOISE ISSUE | VIGNESH | SELVAN | 24:00 | 2:00 | REMOVED TVE ICE AND EVP FAN SAFETY COVER . WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 8:00 | 120260641 | 120260324 | 2 | AMC | NESTO | AJF | AJM | BUTCHERY STEEL BODY CHILLER DOOR ISSUE | RACEL |  | 8:31 | 10:20 | RECTIFY THE DOOR HOLDER AND FIXED. UNIT DOOE NOW OKAY. BUT RECOMMEND TO CHANGE | NEED: AKO CONTROLLER-1, DOOR 750MM*173MM |  | ATTENDED | NEED MATERIAL
2026-01-21 | 11:37 | 120260642 | 120260339 | 1 | AMC | NESTO | SATWA | DXB | ISLAND FREEZER NOISE ISSUE | SHAFI | MUSTAFA | 17:15 | 19:15 | REPLACED THE NEW BOLT FOR FAN MOTOR. ADJUST THE BLADE |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 14:03 | 120260643 | 120260340 | 1 | AMC | NESTO | AJE | AJM | INSPECTION OF HOT FOOD SWEAT COUNTER, BAKERTY COUNTER AND DISPLAY CHILLERS | SABITH ALI | BIJU | 23:10 | 23:45 | SWEAT CHILLER ADJUST THE PARAMETER SETTINGS AND WORKING NORMAL / VERTICAL CHILLER DOOR GASKET DAMAGE FIXED IT TO THE FRAME PROPELY AND OKAY |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 20:49 | 120260644 | 120260341 | 1 | AMC | NESTO | MUWAILHA | SHJ | FREEZER HEADER CABINET NOISE ISSUE | VIGNESH | SELVAN | 3:25 | 4:00 | REMOVED THE ICE FOR EVP COIL AND BACK SIDE NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 12:39 | 120260645 | 7100292743 | 2 | AMC | ENOC | 1239 | AJM | INSIDE WALKIN CHILLER LIGHT NOT WORKING | [7 empty] | ATTENDED | ATTENTED ON 24/1/26
2026-01-21 | 12:39 | 120260646 | 7100292887 | 1 | AMC | ENOC | ZOOM4052 | DXB | Chiller 02 for chilled item not working | SARAVANAN |  | 17:30 | 18:40 | REPLAVED THE DAMAGED FAN MOTOR AND AND RESTART TH UNIT WORKING NORMAL | USED: 16W FAN MOTOR-1, 10W FAN MOTOR-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-21 | 12:39 | 120260647 | 7100292891 | 1 | AMC | ENOC | 1012 | DXB | Walk in freezer temperature is high | SADAM | ZALAUDDIN | 17:30 | 19:20 | REPLACED THE DEFECTIVE CONTACTOR, OVERLOAD AND RETSRT THE UNIT WORKING NORMAL | USED: SCHNIEDER 25AMPS CONTACTOR-1, OVERLOAD LRD14-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-21 | 8:57 | 120260648 | 7100292304 | 2 | AMC | ENOC | 1099 | DXB | Vertical Chiller for Flower | SARAVANAN |  | 9:55 | 10:00 | VERTICAL CHILLER NOT OUR SCOPE |  |  | ATTENDED | NOT OUR SCOPE
2026-01-21 | 11:55 | 120260649 | 7100292284 | 2 | AMC | ENOC | 1007 | DXB | CHILLER LIGHT | SARAVANAN |  | 11:55 | 12:05 | REPLACED THE LIGHT AND UNIT WORKING NORMAL | USED: 4FT LED LIGHT-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-21 | 13:26 | 120260650 |  | 0 | AMC | ENOC | 1125 | SHJ | OPEN CHILLER TEMP ISSUE | VIGNESH | SELVAN | 22:10 | 22:40 | CHECKED CHILLER WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 14:05 | 120260651 |  | 0 | AMC | ENOC | 1033 | DXB | WALKIN FREEZER GASKET NEED TO CHECK AND ICE FORMATION | SHAFI | MUSTAFA | 15:45 | 16:15 | ADJUSTED THE DOOR LOCK AND OBSERVED, CLEANED THE ICE FROM THE CURTAIN AND FRAME |  |  | COMPLETED | WORK COMPLETED
2026-01-21 | 19:20 | 120260652 | 7100292517 | 2 | AMC | ENOC | 1035 | DXB | WALK-IN CHILLER DOOR NOT CLOSING | SHAFI | MUSTAFA | 20:00 | 21:00 | REPLACED NEW DOOR GASKET, CLEANED THE RUSTY DOOR HINGES AND APPLIED OIL LUBRICANT ON HINGES | USED: DOOR GASKET-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-21 | 11:45 | 120260653 | 7100291135 | 3 | AMC | ENOC | 1511 | FUJ | 1 BUSTED LIGHTED LIGHT IN PRONTO DISPLAY | VIGNESH | SELVAN | 23:45 | 24:10 | FIX THE NEW LIGHT AND WORKING NORMAL | USED: 2FT LIGHT 18W-1 BY TD |  | COMPLETED | WORK COMPLETED
2026-01-21 | 20:51 | 120260654 | 120260342 | 1 | AMC | ADNOC | 523 | AUH | CONVOTHERM NOT WORKING
2026-01-21 | 20:00 | 120260655 | MINA PROJECT | 9 | AMC | AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | ROGER | GOVIND, SUDHEESH, ABIJITH | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-21 |  | 120260656 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 9:30 | 19:35 | DIERA MATERIAL COLLECTION, GRANDIOSE SOYOUH, GREEN TERRA MATERIAL COLLECTION AND DELIVER IN WARE HOIUSE, DIERA PANIKEER |  |  | COMPLETED | WORK COMPLETED
2026-01-22 | 9:45 | 120260657 | 120260106 | 2 | AMC | CAREEM | JLT | DXB | FREEZER NO. 06 HIGH TEMP . | SADAM | ZALAUDDIN/SARAVANAN | 9:45 | 12:25 | PULL OUT THE CABINET TO WAREHOUSE AND AFTER REPAIRED WE DELIVERD | FILTER DRIER 1/4-1 , R 290 - 1 , NITROGEN,- BY TD |  | COMPLETED | WORK COMPLETED
2026-01-22 | 8:00 | 120260658 | 120260315 | 3 | AMC | WESTLAND | AL AIN | AL AIN | CHILLER CDU ICE FORMATION IN PIPE LINE | SHAFI | TALIB/MUSTAFA | 11:45 | 14:05 | NEED TO BE CHANGE PRESSUER CUT SWITCH FOR GAS CONTROLL AND DEFROST | PRESSUER CUT SWITCH KP 5 -1, FLEXIBLE HOSE - 2 MTR, NPT NUT - "T" - 1 |  | ATTENDED | ATTENDE ON 23/1/2025
2026-01-22 | 8:06 | 120260659 | 120260343 | 1 | AMC | TCS | RP HEIGHT | DXB | DAIRY CHILLER HAS ICE FORMATION | MOHAMMED | MUTHUKUMAR | 19:55 | 21:45 | REMOVE THE ICE FROM THE EVP COIL BY HEAT WATER AND DOOR MAKE ADJUST IS OKAY. CHILLER CABINET WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-22 | 10:27 | 120260660 | 120260344 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | BUTCHERY CHILLER HIGH TEMP. | SABITH ALI | BIJU | 11:35 | 12:10 | UNIT CHECKED WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-22 | 15:16 | 120260661 | 120260345 | 1 | AMC | BAQER MOHEBI | AL NADHA | DXB | COMBI FREEZER PORK SECTION | VIGNESH | SELVAN | 18:50 | 19:30 | SOCKET DAMAGE AND NEED TO REPLACE SOCKET | INFORMED TO STORE MANAGER |  | COMPLETED | WORK COMPLETED
2026-01-22 | 16:43 | 120260662 | 120260346 | 1 | AMC | TCS | UMS | DXB | PORK FREEZER TEMP ISSUE | VIGNESH | SELVAN | 20:10 | 24:10 | CHANGED THE CONTROLLER NOW WORKING NORMAL | USED:- CONTACTOR LC1D25B7-1NOS |  | COMPLETED | WORK COMPLETED
2026-01-22 | 9:24 | 120260663 |  | 0 | AMC | ENOC | 1012 | DXB | WALK IN FREEZER TEMP. ISSUE | SADAM | ZALAUDDIN | 13:15 | 17:40 | REPLACED THE CONTECTER AND OVERLOADER | USED:- LC1D12M - 1, OVER LOADER LRD14-1 |  | COMPLETED | WORK COMPLETED
2026-01-22 | 11:35 | 120260664 | 7100292579 | 3 | AMC | ENOC | ZOOM4009 | DXB | CHILLER WATER LEAK | SABITH ALI |  |  |  | ATTENDED |  |  | ATTENDED | ATTENDED ON 23JAN26
2026-01-22 | 12:21 | 120260665 |  | 0 | AMC | ENOC | 1142 | SHJ | VERTICAL FREEZER TEMP. ISSUE | RACEL |  | 21:27 | 23:55 | REPLACED NEW FAN MOTOR UNIT NOW WORKING NORMAL | USED:- 25 WATT FAN MOTOR-1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-22 | 20:14 | 120260666 | 120260327 | 2 | AMC | TCS | UMS | DXB | F & V CHILLER NOT WORKING | VIGNESH | SELVAN | 20:10 | 24:10 | REPLACED FAN MOTOR | USED:- AXIAL FAM MOTOR 400MM 220V -1NOS |  | COMPLETED | WORK COMPLETED
2026-01-22 | 22:00 | 120260667 | 120260317 | 2 | AMC | LULU | DIP | DXB | FREEZER CABINET GAS LEAK | MOHAMMED | MUTHUKUMAR | 23:10 | 1:30 | CHANGED THE FILTER DRIER AND AFTER VACCUM UNIT NOW WORKING NORMAL | USED:- FILTER DRIER 3/8-1NOS |  | COMPLETED | WORK COMPLETED
2026-01-22 | 20:00 | 120260668 | MINA PROJECT | 9 | AMC | AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | ROGER | GOVIND, SUDHEESH, ABIJITH | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-22 |  | 120260669 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 8:50 | 18:30 | CAREEM JLT CABINET DELIVERY, CAOLRFLEX AL QUSAIS MATERIAL COLLECTION AND EPT DIP WAREHOUSE DELIVERY AND TRANSPORT |  |  | COMPLETED | WORK COMPLETED
2026-01-22 | 8:00 | 120260670 | 120260236 | 3 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | BREAKER FALIUR | RANDOLPH | TROVEE | 8:40 | 10:05 | CHANGED THE BREAKER NOW SYSTEM IS WORKING NORMAL | CIRCUIT BREAKER LY540406 400A-1NOS |  | COMPLETED | WORK COMPLETED
2026-01-23 | 7:12 | 120260671 | 120260347 | 1 | AMC | CAREEM | ARJAN | DXB | FREEZER TEMP. ISSUE | SADAM | ZALAUDDIN | 8:40 | 9:55 | CHANGED THE FAN MOTOR WORKING NOW NORMAL | USED:- 25W FAN MOTOR-01NOS |  | COMPLETED | WORK COMPLETED
2026-01-23 | 9:57 | 120260672 | 120260348 | 1 | AMC | CAREEM | JLT | DXB | FREEZER TEMP ISSUE | SARAVANAN |  | 11:15 | 13:25 | TOP UP THE R404 GAS NOW SYSTEM WORKING NORMAL TEMP. |  |  | COMPLETED | WORK COMPLETED
2026-01-23 | 11:27 | 120260673 | 120260349 | 2 | AMC | ANSAR | KARAMA | DXB | FREEZER COLD ROOM HIGH TEMP | SABITH ALI | BIJU | 16:10 | 17:30 | FOUND ICE FORMATION IN COIL /REMOVED ICE NEDD SENSERS | NEED:- SENSERS - 2NOS |  | ATTENDED | NEED MATERIAL
2026-01-23 | 9:39 | 120260674 | 7100293177 | 1 | AMC | ENOC | 2020 | DXB | VERTICAL FREEZER TEMP NOT WORKING | SADAM | ZALAUDDIN | 11:00 | 11:20 | WHEN WE VISIT SYSTEM IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-23 | 9:39 | 120260675 | 7100293241 | 1 | AMC | ENOC | 1013 | DXB | OPEN CHILLER BOTTOM AREA IS TOO RUSTY | SARAVANAN |  | 16:15 | 16:25 | CHECKED THE COIL TRAY NEED TO RE PAINT | NEED:- SILVER PAINT - 5 NOS |  | ATTENDED | NEED MATERIAL
2026-01-23 | 11:44 | 120260676 | 120260350 | 1 | AMC | BAQER MOHEBI | VILLA | DXB | COLD ROOM WATER LEAK | SARAVANAN |  | 14:45 | 15:15 | OBSERV THE COLD ROOM HUMIDITY WATER LEAK ITS NORMAL THING |  |  | COMPLETED | WORK COMPLETED
2026-01-23 | 9:00 | 120260677 | 7100292579 | 3 | AMC | ENOC | ZOOM4009 | DXB | CHILLER WATER LEAK | SABITH ALI | BIJU | 11:35 | 13:40 | DRAIN FLOAT SWITCH REMOVED AND INSTALLED TIMMER NOW WORKING NORMAL | USED:-MECANICAL TIMMER-1NOS |  | COMPLETED | WORK COMPLETED
2026-01-23 | 13:48 | 120260678 | 120260351 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | ALL FREEZER TRIPPING ISSUE | RANDOLPH | TROVEE | 14:40 | 17:00 | FOUND FRAME HEATER SHORTED AFTER FIXED NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-23 | 12:24 | 120260679 | 120260352 | 2 | AMC | GOURMET | 1004 | AUH | PORKSECTION FREEZER TEMP ISSUE | OLIVER | FROILAN | 14:33 | 15:15 | FOUND UNIT COMPRESSOR DEFFECTIVE NEED TO CHANGE | NEED:- COMPRESSOR CAJ2446Z FLARE TYPE-1NOS, FILTER DRIER 3/8 SD-1NOS, GAS 404-1CYLD,BREZING ROD -2 STICK. |  | ATTENDED | ATTENDED ON 30/1/2026
2026-01-23 | 14:25 | 120260680 |  | 0 | AMC | ENOC | 412 | DXB | VERTICAL FREEZER AND OPEN CHILLER INSPECTION | SHAFI | MUSTAFA | [5 empty] | COMPLETED
2026-01-23 | 15:42 | 120260681 |  | 0 | AMC | ENOC | 1063 | DXB | BED FREEZER INSULATION CHANGE | [7 empty] | COMPLETED | PPM FINDING
2026-01-23 | 18:11 | 120260682 | 120260353 | 1 | WTY | ADNOC | 750 | FUJ | TEMP.ISSUE | VIGNESH | SELVAN | 20:00 | 22:30 | FIND CONDENSER BLOCK . CLEAR THE CONDENSER NOW SYSTEM WORK NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-23 | 18:35 | 120260683 | 120260354 | 1 | AMC | AD COOP/DEYAAR | SPAR ELECTRA | AUH | EGG CHILLER NOT WORKING | RANDOLPH | TROVEE | 19:40 | 20:30 | DEFECTIVE SOCKET AND NEED TO REPLACE | SOCKET CHANGE BY DEYAAR |  | COMPLETED | WORK COMPLETED
2026-01-23 | 18:11 | 120260684 | 120260355 | 1 | WTY | ADNOC | 750 | FUJ | OPEN CHILLER LIGHT NOT WORKING | VIGNESH | SELVAN | 20:00 | 22:30 | FOUND LED DRIVE COMPLENT | NEED:- LED DRIVE FS-HY-60H-24 - 1NOS |  | ATTENDED | NEED MATERIAL
2026-01-23 | 23:07 | 120260685 | 120260356 | 1 | AMC | NESTO | AJE | SHJ | EGG CHILLER NOT WORKING | VIGNESH | SELVAN | 24:10 | 1:10 | SINGLE POLE BRAKER HAS TRIPPING /AFTER WE RESET THE BRAKER SYSTEM NOW WORKING |  |  | COMPLETED | WORK COMPLETED
2026-01-23 | 11:27 | 120260686 | 120260349 | 2 | AMC | ANSAR | KARAMA | DXB | FREEZER COLD ROOM TRMP. ISSUE | MOHAMMED | MUTHUKUMAR | 23:30 | 24:45 | REMOVED THR OLD SENSER AND AFTER INSTALLING NE SENSER NOW SYSTEM UNDER OBSERVETION | USED:- SENSER -2NOS [NEED:- PVC CURTTEN-6NOS,DOOR L FRAME-1NOS 2X2, MAICA SHEET 1MM - 1NOS |  | ATTENDED | NEED MATERIAL
2026-01-23 | 14:00 | 120260687 | 120260357 | 1 | AMC | CAREEM | WAREHOUSE JEBEL ALI | DXB | CHEST FREEZER TEMP. ISSUE | SADAM |  | 15:00 | 17:30 | FOUND COMPRESSOR TO BE REPLACE | NEED:- COMPRESSOR HUAGUANG FTA55L -1NOS,GAS 290-1CYLD, 1/4 FILTER DRIER-1NOS, CHARGING PIN-1NOS, NITROGRN SMALL-1CYLD, COPPER ROD- 2 STICK, BLUE ROD- 2NOS |  | ATTENDED | NEED MATERIAL
2026-01-23 | 15:00 | 120260688 | 120260315 | 3 | AMC | WESTLAND | AL AIN | AL AIN | NO.05 UNIT ICE FORMATION | AHSAN | TALIB | 16:00 | 21:30 | CHANGED THE PRESSUER SWITCH AND FLEXIBLE HOSE NOW OUT DOOR UNIT IS NORMAL | USED:- PRESSURE SWITCH KP5-1NOS, MPT T NUT-1NOS,AND FLEXIBLE HOUSE-1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-23 | 1:56:00PM | 120260689 | 720250294 | 1 | AMC | ANSAR | KARAMA | DXB | NEED TO CHANDE CONDENSOR FAN MOTOR | SABITH ALI | [6 empty] | ATTENDED
2026-01-23 | 8:00:00PM | 120260690 | MINA PROJECT | 9 | AMC | AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | ROGER | GOVIND, SUDHEESH, ABIJITH | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-23 |  | 120260691 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 6:50 | 20:00 | AJMAN PORT,GRNDIOSE AL SOUYAH,BARAD ATLANDA,DIP-1 |  |  | COMPLETED | WORK COMPLETED
2026-01-23 |  | 120260692 | PPM | 37 | AMC | AMAZON | DXB 3 | DXB | Q1 | ABID | RANJITH, SHAHABUDDIN | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-24 | 6:26 | 120260693 | 120260358 | 2 | AMC | CAREEM | AL SAFA | DXB | CHILLER HIGH TEMP. | SADAM |  | 9:30 | 11:00 | THERE IS A COMPRESSOR NEED TO BE REPLACE | NEED:- COMPRESSOR KULTHORN AW7512Z -1NOS,404 -1CYILS,NITROGEN SMALL-1NOS,1/4 FILTER DRIER SD TYPE,CHANRGING PIN-1NOS,BLUE ROD-2 STICK,COPPER ROD -2NOS |  | ATTENDED | NEED MATERIAL
2026-01-24 | 10:30 | 120260694 | 120260359 | 1 | AMC | NESTO | AJJ | AJM | CHILLER SENSOR COMPLAINT FISHERY | RACEL |  | 14:00 | 19:16 | CHANGED LIMIT SWITCH AND FIBRICATED L STOPER | USED:-LIMIT SWITCH / NEED :- DOOR HANDLE SET |  | ATTENDED | NEED MATERIAL
2026-01-24 | 11:33 | 120260695 | 120260360 | 1 | AMC | NESTO | ARJAN | DXB | ICE FORMATION | SADAM |  | 14:00 | 15:00 | REMOVED THE ICE AND CLEAN THE EVAPORATER ND MAKED DEFROST MANUELY NOW SYSTEM IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-24 | 11:42 | 120260696 | 120260361 | 1 | AMC | NESTO | AL AIN | AL AIN | FREEZER LOW COOLING | TALIB |  | 1:00 | 3:25 | ICE FORMATION IN EVAPORATOR AFTER CLEANING ICE NOW SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED | 25/1/2026 WORKED IN NIGHT
2026-01-24 | 9:00 | 120260697 | 120260362 | 1 | AMC | NESTO | WAREHOUSE | DXB | DOOR LOCK NOT WORKING | SADAM |  | 11:30 | 12:24 | FOUND ICE FORMATION /AFTER REMOVE ICE SYSTEM WORKING NORMAL | NEED:- PVC CURTTIN 2MTR - 8 NOS |  | ATTENDED | NEED MATERIAL
2026-01-24 | 12:08 | 120260698 | 120260363 | 2 | AMC | GRANDIOSE | B1 MALL | DXB | FREEZER NOT WORKING | SHAFI |  | 14:30 | 20:45 | FIND OUT THE LEAK IN U BEND AFTER REPAIR AND GAS CHARGED WORKING NORMAL | USED:- R 404 -3NOS |  | COMPLETED | WORK COMPLETED | WORK COMPLETED (ON 25/1/2025)SECONED LEAK ARREST
2026-01-24 | 12:42 | 120260699 | 120260364 | 1 | AMC | AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | BAKERY DISPLAY NOT WORKING | AHSAN |  | 17:00 | 17:40 | FIND OUT THE COMPRESSOR WORKING CONTUNIESLY NEED TO CHANG CONTROLLER | NEED:- DIXEL XR06CX -1NOS,9 AMP CONTACTOR-1 NOS. |  | ATTENDED | NEED MATERIAL
2026-01-24 | 8:20 | 120260700 | 120260164 | 2 | AMC | HOP | JEBAL ALI | DXB | FREEZER COLD ROOM DOOR CHECK | SARAVANAN | ZALAUDIN | 9:30 | 12:15 | REMOVED THE OLD HEATER AND REPLACED NEW HEATER NOW WORKING NORMAL |  | USED:- DOOR HEATER 220V-1 NOS | COMPLETED | WORK COMPLETED
2026-01-24 | 10:05 | 120260701 | 120260365 | 1 | AMC | NESTO | AJF | AJM | DOOR SWITCH CHECK IN COLD ROOM | AHSAN |  | 10:00 | 13:00 | FIXED DOOR SWITCH NEW | USED:- SINGLE GAGE SWITCH-1NOS,1.5MM WIRE 6MTR,SWITCH BOX - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-24 | 13:28 | 120260702 | 120260366 | 1 | WTY | NESTO | FAKRUDDIN MALL | AJM | ICE MACHINE LESS PRODUCTION | AHSAN |  | 14:20 | 15:30 | FOUND ICE BIN IS FULL /REMOVED ICE FROM BIN AND CLEAND CONDENSER NOW ICE FORMATION IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-24 | 9:00 | 120260703 | 7100292743 | 2 | AMC | ENOC | 1239 | AJM | INSIDE WALKIN CHILLER LIGHT NOT WORKING | RACEL |  | 10:20 | 13:25 | REMOVED OLD LIMIT SWITCH AND REPLACED NEW ONE NOW WORKING LIGHT NORMAL | USED:- LIMIT SWITCH BY TD |  | COMPLETED | WORK COMPLETED
2026-01-24 | 13:00 | 120260704 | 120260367 | 1 | PAYABLE | LULU | TCA | AUH | FROZEN VEG.PLUG IN UNIT TEMP. ISSUE | RANDOLPH | TROVEE/OLIVER | 14:20 | 15:05 | FOUND OUT COMPRESSOR AT THE RIGHT SIDE AREA WAS LOW PUMPING IN THE CASEMECHANICAL WAS DEFECTIVE | NEED:- COMPRESSOR -1NOS SECOP SC21CNX.2,FILTER DRIER 1/4-1NOS,NITROGEN BIG-1 NOS,ACCESS VALVE-2NOS. |  | ATTENDED | NEED MATERIAL
2026-01-24 | 15:13 | 120260705 | 120260368 | 1 | AMC | TCS | UMS | DXB | ICECREAM FREEZER NOT WORKING | MOHAMMED | MUTHUKUMAR | 23:00 | 3:00 | CLEAN THE COIL AFTER WATER SERVICE NOW SYSTEM WORKING NORMAL | NEED :- FAN MOTOR |  | ATTENDED | NEED MATERIAL
2026-01-24 | 13:44 | 120260706 | 7100293317 | 1 | AMC | ENOC | 1142 | SHJ | WATER DRIPPING IN WALK IN FREEZER | VIGNESH | SELVAN | 24:37 | 1:07 | WATER DRIPPING FROM DRINEGE NEED TO SUTDOWN |  |  | ATTENDED | NEED TO SCHEDULE
2026-01-24 | 13:44 | 120260707 | 7100293384 | 2 | AMC | ENOC | 1017 | DXB | ABOVE THE OPEN CHILLER CABINET SHELF BOT | SARAVANAN | SHABEEB | [5 empty] | ATTENDED | ATTENDED ON 2/2/26
2026-01-24 | 13:44 | 120260708 | 7100293390 | 2 | AMC | ENOC | 1039 | DXB | ICE FORMING IN WALK IN FREEZER | MOHAMMED | [6 empty] | ATTENDED | ATTENDED ON 25/01/26
2026-01-24 | 13:44 | 120260709 | 7100293418 | 2 | AMC | ENOC | 412 | RAK | TESTING,AND INSTALLATION OF THE VERTICA | SHAFI | MUSTAFA | [5 empty] | COMPLETED
2026-01-24 | 15:32 | 120260710 | 120260369 | 3 | AMC | CAREEM | MARINA | DXB | OPEN CHILLER NOT WORKING | SADAM |  | 17:35 | 18:20 | SYSTEM TRIPPED TRUN ON THE BRAKER NOW SYSTEM OBSERVATION |  |  | COMPLETED | WORK COMPLETED
2026-01-24 | 17:40 | 120260711 | 120260370 | 2 | AMC | AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER AND BUCHERY CHILLER TEMP.ISSUE | RANDOLPH | TROVEE | 18:40 | 20:30 | FOUND OUNT DUAL PRESSUR SWITCH DEFECTIVE | USED:- R404A-1CYLD,DUAL PRESUER SWITCH KP15 AUTO-1NOS. BY DEYAAR. |  | ATTENDED | ATTENDED ON 25/1/2026
2026-01-24 | 18:03 | 120260712 | 120260371 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | CHILLER TEMP ISSUE | VIGNESH | SELVAN | 18:40 | 21:00 | FIND OUT THE PIPE LINE GAS LEACKING AFTER REPAIRED AND GAS CHARGE SYSTEM NOW NORMAL WORKING | USED:- GAS 404 - 5 KG |  | COMPLETED | WORK COMPLETED
2026-01-24 | 22:23 | 120260713 | 120260372 | 3 | AMC | AD COOP/DEYAAR | AWQAF | AUH | VEG. CHILLER POWER OFF | FROILAN | OLIVER | [5 empty] | ATTENDED | ATTENDED ON 25/1/2026
2026-01-24 | 11:24:00:PM | 120260714 | 120260373 | 1 | AMC | AD COOP/DEYAAR | BANIYAS CENTER | AUH | FREEZER NOT WORKING | RANDOLPH | TEOVEE | 24:05 | 1:05 | FOUND ICE FORMATION .AFTER REMOVE ICE AND SET THE DEFROSTING TIME NOW SYSTEM WORKING NORMAL | NEED:- PT 100 SENSOR-2 NOS |  | ATTENDED | NEED MATERIAL
2026-01-24 | 20:44 | 120260715 | 120260374 | 1 | AMC | PASONS | FUJAIRAH | FUJ | JUICE CHILLER HIGH TEMP | VIGNESH | SELVAN | 21:50 | 23:30 | FIND OUT THE COMPRESSOR DEFECT | NEED :- COMPRESSOR-COPLEND-CR53KQM-TED-201-1NOS,FILTER DRIER-3/8-1NOS,GAS-R22-1NOS,CONTACTOR-LC1D32M7-32A-1NOS. |  | ATTENDED | NEED MATERIAL
2026-01-24 | 20:45 | 120260716 | 120260375 | 2 | AMC | CAREEM | DSO | DXB | FREEZER GLASS DOOR ISSUE | [7 empty] | ATTENDED | ATTENDED ON 26/1/2026
2026-01-24 | 22:00 | 120260717 | 120260369 | 3 | AMC | CAREEM | MARINA | DXB | OPEN CHILLER NOT WORKING | MOHAMMED | MUTHUKUMAR | 23:30 | 2:00 | AFTER CHECKING WIREING IDENTIFY DRAIN DRY HEATER DAMAGEFOR TEMP. DISCONNECTED UNIT NOW UNDER OBSERVATION | USED:- CONDENSER FAN MOTOR 16W-1 NOS BY TD/NEED :- DRAIN HEATER-1 NOS |  | ATTENDED | NEED MATERIAL
2026-01-24 | 8:00:00PM | 120260718 | MINA PROJECT | 9 | AMC | AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | ROGER | GOVIND, SUDHEESH, ABIJITH | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-24 |  | 120260719 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 8:30 | 19:15 | AMAZON DXB3,DIP 1,SHAJ IND 4,MATIREAL PURCHACE |  |  | COMPLETED | WORK COMPLETED
2026-01-24 |  | 120260720 | PPM | 37 | AMC | AMAZON | DXB 3 | AUH | Q1 | ABID | RANJITH, SHAHABUDDIN | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-25 | 11:00:00: PM | 120260721 | 7100293390 | 2 | AMC | ENOC | 1039 | DXB | ICE FORMING IN WALK IN FREEZER | MOHAMMED | MUTHUKUMAR | 1:35 | 2:25 | REMOVED ICE FORMATION FROM TOP CEILING AFTER RESETTING NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED | 25/1/2026 NIGHT ATTENDED
2026-01-25 | 17:48 | 120260722 | 120260370 | 2 | AMC | AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER AND BUCHERY CHILLER TEMP.ISSUE | OLIVER | FROILAN/WILLIOM | 16:48 | 18:20 | COMPRESSOR IS NOT FUNTION AND TRIP ISSUE. AFTER HIGH PRESSUER SWITCH MONITOR UNIT IS NOW NORMAL WORKING |  |  | COMPLETED | WORK COMPLETED
2026-01-25 | 12:00 | 120260723 | 120260363 | 2 | AMC | GRANDIOSE | B1 MALL | DXB | FREEZER NOT WORKING | SHAFI | MUSTAFA | 13:15 | 20:50 | FOUND LEACK IN TOP OF CABINET AND BOTTOM OF CABINET AFTER REPROSSES NOW SYSTEM WORKING NORMAL | USED:- GAS 404 - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-25 | 22:23 | 120260724 | 120260372 | 3 | AMC | AD COOP/DEYAAR | AWQAF | AUH | VEG. CHILLER POWER OFF | FROILAN | OLIVER | 9:19 | 10:30 | FOUND COMPESSOR DAMEGE | NEED:-EMBRACO COP.-NT6226GK-1 NOS,FILTER DRIER-1/4-1NOS,GAS-404-1NOS,141B-1NOS,BITROGEN BIG,ACCESS VALVE-2NOS,BRESSIG ROD-2 STICK, BLUE ROD-1 NOS. |  | ATTENDED | NEED MATERIAL
2026-01-25 | 9:00 | 120260725 | 120260376 | 1 | AMC | LULU | DIP | DXB | FREEZER 21 ITEMS IN TOP MELTING(TEMP NORMAL) |  |  |  |  | CLINT INFORMED UNIT IS WORKING NORMAL |  |  | NOT ATTENDED | CANCELLED
2026-01-25 | 10:04 | 120260726 | 120260377 | 1 | AMC | CAREEM | MOTOR CITY | DXB | CHEST FREEZER NOT WORKING | MOHAMMED | MUTHUKUMAR | 19:00 | 21:30 | AFTER REFIXING UNIT NOW CHEST FREEZER IS WORKING NORMAL | USED:- LED LIGHT -1 NOS,LED LIGHT - T8-2NOS/NEED:- LED LIGHT STRIP - 1NOS 4 FEET |  | ATTENDED | NEED MATERIAL
2026-01-25 | 11:00 | 120260727 | 120260369 | 3 | AMC | CAREEM | MARINA | DXB | BRAKER TRIPING | SARAVANAN |  | 17:11 | 17:45 | CHANGED BREAKER 32 AMP. | NEED:- 32 AMPS 2 POLE BRAKER-1NOS |  | COMPLETED | WORK COMPLETED
2026-01-25 | 12:58 | 120260728 | 120260378 | 1 | AMC | CAREEM | JLT | DXB | FREEZER TEMP. ISSUE | SARAVANAN |  | 15:00 | 16:00 | CHECKED THE CABINET NEED TO BR RE PROCESS THE SYSTEM | NEED:- R404A-1NOS,FILTER DRIER 1/4-1 NOS, SERVICE PIN-1NOS,1/4 COPPER PIPE-1 MTR. |  | ATTENDED | NEED MATERIAL | NEED TOBE RE PROCESS
2026-01-25 | 13:57 | 120260729 | 120260379 | 1 | AMC | CAREEM | JVT | DXB | INDOOR NEED TO SERVICE
2026-01-25 | 16:18 | 120260730 | 120260380 | 2 | AMC | BAQER MOHEBI | AL NADHA | SHJ | MILK CHILLER WATER LEAK | VIGNESH | [6 empty] | ATTENDED | ATTENDED ON 26/1/2026
2026-01-25 | 20:29 | 120260731 | 120260381 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | CHILLER HIGH TEMP. VEG CHILLER LIGHT NOT WORKING | MOHAMMED | MUTHUKUMAR | 20:40 | 24:35 | AFTER GAS TOPUP AND CHANGING LIGHT NOW SYSTEM WORKING NORMAL | USED:- R 22GAS-1 NOS,LED LIGHT SET-1NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-25 | 11:44 | 120260732 | 120260382 | 1 | AMC | AD COOP/DEYAAR | SPAR SAADIAYT | AUH | BAKERY AND HOT MEAT DISPLAY CHILLER TRIP ISSUE. | OLIVER | FROILAN/WILLIOM | 12:41 | 13:20 | AFTER RESET BRAKER TWO UNITS ALSO WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-25 | 16:25 | 120260733 | 120260383 | 1 | AMC | AD COOP/DEYAAR | MADINAT ZAYED | AUH | ALL FREEZER NOT WORKING | OLIVER | FROILAN/WILLIOM | 18:46 | 19:51 | FOUND OUT THE TRIP OFF DUE TO THE ELECTRICAL FAULT AFTER POWER ON ALL UNITS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-25 | 9:25 | 120260734 | 120260384 | 1 | AMC | NESTO | SATWA | DXB | FREEZER NOT COOLING | RACEL |  | 10:38 | 13:46 | CHANGED THE EVAP0RATOR FAN MOTOR CASE OFF NOW AIR FLOW .NOW SYSTEM IS NORMAL WORKING | USED:- 10W FAN MOTOR-1NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-25 | 10:02 | 120260735 | 120260385 | 2 | WTY | ADNOC | 750 | FUJ | HIGH TEMP. | RACEL | [6 empty] | ATTENDED | ATTENDED TWO COPMLENTS
2026-01-25 | 12:06 | 120260736 | 120260386 | 1 | WTY | ADNOC | 435 | RAK | VERTICAL FREEZER HIGH TEMP | RACEL |  | 16:46 | 18:10 | ICE FORMATION IN COIL AFTER REMOVE ITEMS DEEP CLEANED THE UNIT AND RE SETTING PARAMETER NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-25 | 12:06 | 120260737 | 120260385 | 2 | WTY | ADNOC | 750 | FUJ | 2 OPEN CHILLER NOT COOLING | RACEL |  | 20:00 | 23:55 | HIGH TEMP. BECOUSE WOOD COVER BLOKED .ALREADY ADVICE TO REMOVE |  |  | COMPLETED | WORK COMPLETED
2026-01-25 | 12:06 | 120260738 | 120260388 | 1 | WTY | ADNOC | 750 | FUJ | GLASS DOOR CHILLER HIGH TEMP. | RACEL |  | 20:00 | 23:55 | HIGH TEMP. BECOUSE WOOD COVER BLOKED .ALREADY ADVICE TO REMOVE |  |  | COMPLETED | WORK COMPLETED
2026-01-25 | 8:00:00PM | 120260739 | MINA PROJECT | 9 | AMC | AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | ROGER | GOVIND, SUDHEESH, ABIJITH | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-26 | 10:38 | 120260740 | 120260390 | 2 | AMC | TCS | ROVE TRADE CENTER | DXB | CHILLERS HIGH TEMP.ISSUE. | SABITH ALI |  | 13:10 | 14:25 | CH-1 IS WORKING NORMAL (ROOM TEMP HIGH),CH-2 CHILLER CONTROLLER NOT WORKING PROPERLY | NEED:- CONTROLLER IPC DANFOSS 202D - 1NOS, CONDENCER FAN 25W-1NOS |  | ATTENDED | NEED MATERIAL
2026-01-26 | 9:19 | 120260741 | 120260391 | 1 | AMC | NESTO | ARJAN | DXB | ICE MACHINE NOT WORKING | SARAVANAN |  | 14:30 | 14:55 | FOUND OUT WATER FILTER TO BE REPLACE |  |  | ATTENDED | NEED MATERIAL
2026-01-26 | 11:23 | 120260742 | 120260392 | 1 | AMC | NESTO | AJE | AJM | CHILLER TEMP.ISSUE | AHSAN |  | 14:50 | 18:00 | FOUND OUT EVAPORATOR LEAK.AFTER FIXED NOW WORKING NORMAL | USED:- R 22 GAS - 1 CYLD |  | COMPLETED | WORK COMPLETED
2026-01-26 | 7:36 | 120260743 | 120260393 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | 2 ICE MACHINES NOT WORKING | FROILAN | OLIVER | 8:43 | 10:00 | FOUND EVAPORATOR CONECTION NOT CORRECT AFTER CONNECTING WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 7:36 | 120260744 | 120260394 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER DOOR GASKET IS DAMAGED | RANDOLPH | TROVEE | 9:10 | 9:40 | DOOR GASKET NEED TO BE CHANGE | NEED:- DOOR GASKET |  | ATTENDED | NEED MATERIAL
2026-01-26 | 8:56 | 120260745 | 120260395 | 1 | AMC | AD COOP/DEYAAR | MBZ | AUH | WATER LEAK
2026-01-26 | 9:48 | 120260746 | 120260396 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | PROOFER TEMP.ISSUE |  |  |  |  | NOT IN OUR SCOOP |  |  | NOT ATTENDED | NOT IN OUR SCOPE
2026-01-26 | 10:56 | 120260747 | 120260397 | 1 | AMC | AD COOP/DEYAAR | SPAR SHABHAT PLAZA | AL AIN | WATER LEAKING FROM OPEN CHILLER NO.3 | TALIB |  | 16:30 | 7:25 | REMOVED THE WATER FROM DRAIN TRAY CHECK THE HEATER IS DAMAGE | NEED:- UPCS DRAIN HEATER 500W - W-7.5 X L- 24 CM |  | ATTENDED | NEED MATERIAL
2026-01-26 | 11:15 | 120260748 | 120260337 | 2 | AMC | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | FAN MOTOR AVAILABLE IN STORE | VIGNESH | SELVAN | 11:50 | 13:13 | found fan motor not working /changed evaporator fan motor now working normal | USED:- FAN MOTOR 10 W-1NOS BY DEYAAR/ NEED:- ENWELL CONTROLLER-EW961-1NOS, LC1D12 - 1NOS |  | ATTENDED | NEED MATERIAL
2026-01-26 | 11:15 | 120260749 | 120260398 | 1 | AMC | AD COOP/DEYAAR | SPAR SHABHAT PLAZA | AL AIN | FREEZER NO 05 TEMP.ISSUE | TALIB |  | 16:50 | 19:25 | THE CABINET IS OVERLOADED AFTER REMOVE ITEMS AND CLEAN CONDENSER NOW SYSTEM IS NORMAL WORKING |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 16:18 | 120260750 | 120260380 | 2 | AMC | BAQER MOHEBI | AL NADHA | SHJ | MILK CHILLER WATER LEAK | VIGNESH | SELVAN | 10:20 | 11:45 | FOUND DRAINAGE LINE DAMAGE WE REPAIRD DRAIN LINE NOW WORKING NORMAL | USED:- M SAL-1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-26 | 7:39 | 120260751 | 120260399 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | BUTCHERY DISPLAY LIGHTS CHILLER NOT WORKING | VIGNESH | SELVAN | 10:20 | 11:45 | NEED TO CHANGE LIGHT | NEED:- LT28 WT 5/840- 4NOS 4FEET / USED:- LT28 WT 5/840- 4NOS 4FEET |  | COMPLETED | WORK COMPLETED | CHANGED SAME DAY 1:40:00 TO 15:00:00
2026-01-26 | 7:42 | 120260752 | 120260400 | 1 | AMC | CAREEM | STAR CITY | DXB | OUT DOOR ICE FORMATION | SHAFI | MUSTAFA | 9:30 | 10:00 | IT IS NORMAL ICE FORMATION BECAUSE THERE IS NO INSULATION IN VINRATION ELIMINATOR |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 8:45 | 120260753 | 120260401 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | CHILLER TEMP. ISSUE | AHSAN |  | 12:30 | 13:25 | FOUND OUT ICE FORMATION AFTER RESETTING DEFROST FUNTION NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 8:52 | 120260754 | 120260402 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | VEG CHILLER 6 NOS LIGHT NOT WORKING | AHSAN |  | 11:30 | 12:30 | FOUND LIGHT CONNECTOR DAMAGE AFTER CHANGE CONECTOR WORKING LIGHTS | USED: FROM STORE |  | COMPLETED | WORK COMPLETED
2026-01-26 | 9:18 | 120260755 | 120260403 | 1 | AMC | CAREEM | UMS | DXB | TEMP.DISPLAY NOT SHOWING | SARAVANAN |  | 16:40 | 17:10 | CHANGED THE THERMOMETER NOW WORKING IS NORMAL | USED:- DISPLAY THERMOMETTER |  | COMPLETED | WORK COMPLETED
2026-01-26 | 12:14 | 120260756 | 120260404 | 1 | AMC | LULU | OLIVE TOWER | AUH | VEGETABLE CHILLER NOT WORKING | TROVEE | RANDOLPH/OLIVER/FROILAN | 12:50 | 13:30 | CHILLER IS NOW WORKING NORMAL NEED TO CHANGE HEATER | NEED:-HEATER 25CM 230V - 1NOS |  | ATTENDED | NEED MATERIAL
2026-01-26 | 12:16 | 120260757 | 120260405 | 2 | AMC | BADIA FARMS | AL QUOZ | DXB | ZONE 3 CHILLER NOT WORKING | [7 empty] | ATTENDED | ATTENDED ON 27/1/2025
2026-01-26 | 10:58 | 120260758 | 7100293482 | 1 | AMC | ENOC | 1080 | DXB | METAL SHEET UNDER THE OPEN CHILLER | SADAM | ZALAUDIN | 1:00 | 2:00 | FIX THE BOTTOM GLADDING METEL SHEET TEMPRORLY . NEED TO CHANGE |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 10:58 | 120260759 | 7100293549 | 1 | AMC | ENOC | 1057 | DXB | BED FREEZER TEMP. READER IS DETACHED | SADAM | ZALAUDIN | 0:12 | 1:15 | BED FREEZER NOT UNDER OUR SCOPE |  |  | ATTENDED | NOT IN OUR SCOPE
2026-01-26 | 10:58 | 120260760 | 7100293594 | 1 | AMC | ENOC | 1126 | SHJ | OPEN CHILLER NOT WORKING PROPERLY | RACEL | BIJU | 21:52 | 24:00 | AFTER CLEANING CONDENSER COIL UNIT IS WORKING NORMAL/ BUT NEED TO CHANGE CONTROLLER | NEED:- DANFOSS EKC 202D CONTROLLER- 1NOS, PT 1000 SENSORS- 2 NOS. |  | ATTENDED | NEED MATERIAL
2026-01-26 | 10:58 | 120260761 | 7100293689 | 1 | AMC | ENOC | 1135 | SHJ | ICE CREAM BED FREEZER NOT WORKING | VIGNESH | SELVAN | 15:40 | 19:10 | FIND OUT THE EVAPORATOR FAN MOTOR NOT WORKING / AFTER REPLACING NOW SYSTEM WORKING NORMAL | USED:- FAN MOTOR 120X 120 - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-26 | 10:58 | 120260762 | 7100293703 | 1 | AMC | ENOC | 1103 | SHJ | WALKIN CHILLER DOOR GASKET DAMAGED | SABITH ALI | [6 empty] | COMPLETED
2026-01-26 | 12:56 | 120260763 | 120260406 | 1 | AMC | AD COOP/DEYAAR | MUROOR | AUH | BAKERY FREEZER NOT WORKING | OLIVER | RANDOLPH | 12:46 | 13:13 | NEED TO COMPRESSOR CHANGE | NEED:- COMPRESSOR -NT2192GK -1NOS, FILTER DRIER 1/4-1NOS,GAS 404 -1NOS,141B -1NOSNITROGEN BIG-1 NOS,ACCESS VALVE 1/4 - 1 NOS, BRASSING ROD - 2 STICK , BLUE ROD - 2 STICK. |  | ATTENDED | NEED MATERIAL
2026-01-26 | 12:56 | 120260764 | 120260407 | 3 | AMC | NESTO | KARAMA | DXB | BUTCHERY CHILLER AND FISHERY CHILLER DISPLAY CHECK | [7 empty] | ATTENDED | ATTENDED ON 27/1/2026
2026-01-26 | 13:39 | 120260765 | 120260408 | 1 | AMC | NESTO | AJE | AJM | F&V CHILLER AND DAIRY SECTION NOT COOLING PROPERLY | RACEL | BIJU | 1:33 | 3:36 | REMOVED THE CABINET COVER CLEANED THE CABINET ABD FLOOR DRAIN NOW UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 13:53 | 120260766 | 120260409 | 1 | AMC | LULU | DIP | DXB | ICE MACHINE NOT WORKING | SHAFI | MUSTAFA | 18:00 | 20:10 | FOUND OUT CONDENSER FAN MOTOR DAMAGE NEED TO REPLACE | NEED:- FAN MOTOR A4E350-AA06-01 230V - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-01-26 | 14:35 | 120260767 | 120260410 | 1 | AMC | NESTO | AJG | AJM | VEGETABLE BACK STORE DOOR NOT CLOSING | AHSAN |  | 18:40 | 19:00 | FOUND OUT THERE IS A MISSING ANGLE /NOW TEMP0RARILY FIXED | NEED:- 3x3 ALUMINNIUM ANGLE 120 CM, SILICON - 1NOS |  | ATTENDED | NEED MATERIAL
2026-01-26 | 12:00 | 120260768 | 120260375 | 2 | AMC | CAREEM | DSO | DXB | FREEZER GLASS DOOR ISSUE | SARAVANAN |  | 13:40 | 13:55 | NEED TO BE REPLACE SLIDING DOORS | NEED:- 2NOS SLIDING DOORS NEED |  | ATTENDED | NEED MATERIAL
2026-01-26 | 15:01 | 120260769 | 120260411 | 1 | AMC | ANSAR | KARAMA | DXB | KICTHEN UNITS ARE NOT WORKING | RACEL | BIJU | 19:14 | 20:25 | WHEN TEAM IS REACH ALL UNITS ARE WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 16:22 | 120260770 | 120260412 | 1 | AMC | AD COOP/DEYAAR | AL MANASIR | AL AIN | FREEZER NO 1 IS NOT WORKING | TALIB |  | 20:20 | 22:35 | DONE WATER SERVICE FOR REMOVE ICE FORMATION NOW SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 17:01 | 120260771 | 120260413 | 1 | AMC | TCS | AL AWEER | DXB | WATER PIPE LINE BLOCK AND LEAKAGE OF WATER IN CHILLER NO 48 | SADAM | ZALAUDIN | 21:45 | 22:15 | SINK DRAINGE PIPE LEAK -NOT IN OUR SCOPE |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 17:01 | 120260772 | 120260414 | 1 | AMC | TCS | EMERALD COURT | DXB | ICE MACHINE HAS SHUT DOWN | SADAM | ZALAUDIN | 19:00 | 21:00 | TRIPPING BECAUSE WATER CONTENT IN PLUG/AFTER CLEANING PLUG NOW SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 17:32 | 120260773 | 120260415 | 1 | AMC | AD COOP/DEYAAR | MUROOR | AUH | SMALL CHILLER DISPLAY IN THE FISH SECTION IS NOT WORKING
2026-01-26 | 17:32 | 120260774 | 120260416 | 1 | WTY | ADNOC | 448 | AUH | CHILLER TEMP. ISSUE | RANDOLPH | TROVEE | 18:33 | 17:30 | CHECKED THE CABINET FOUND SWITCH OFF/AFTER SWITCH ON SYSTEM IS NORMAL WORKING |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 17:32 | 120260775 | 7100293001 | 2 | AMC | ENOC | 1079 | DXB | CHILLER DOOR HANDLE BROKEN | SARAVANAN |  | 18:40 | 19:00 | FOUD OUT DOOR HANDEL CAN'T REPAIR NEED TO REPLACE | NEED:- DOOR HANDEL |  | ATTENDED | NEED MATERIAL
2026-01-26 | 19:31 | 120260776 | 120260417 | 1 | AMC | NESTO | AJG | AJM | DISPLAY FREEZER ICE FORMATION | RACEL | BIJU |  |  | COUSTUMER NOT REMOVED ITEMS |  |  | NOT ATTENDED | RESCHEDULE
2026-01-26 | 12:00 | 120260777 | 7100293418 | 2 | AMC | ENOC | 412 | RAK | TESTING,AND INSTALLATION OF THE VERTICA | SHAFI | MUSTAFA | 13:30 | 16:20 | CHILLER AND FREEZER CLEAND THE CONDENSOR CLEANED NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-26 | 9:00 | 120260778 | 720251252 | 1 | AMC | LULU | AL KAHIR | AL AIN | EVALUATION OF USE AND OLD LUGIN FREEZER CABINET | TALIB |  | 10:00 | 19:50 | DOUBLE CHECK OTHER PARTS OF CABINET AND FOUND COMPLETE, NEED END PANEL OF THE UNIT | USED: END PANEL (LEFT SIDE)-1, SILICON-3 |  | COMPLETED | WORK COMPLETED
2026-01-26 | 22:02 | 120260779 | 120260435 | 2 | WTY | PASONS | FUJAIRAH | FUJ | COMPRESSOR REPLACEMNET | SABITH ALI |  |  | 21:02 | REMOVED FOR WARRENTY |  |  | ATTENDED | NEED MATERIAL
2026-01-26 | 8:00:00PM | 120260780 | MINA PROJECT | 9 | AMC | AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | ROGER | GOVIND, SUDHEESH, ABIJITH | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-26 |  | 120260781 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 7:45 | 20:20 | DUBAI TO AJMAN, AJMAN INDUSTREAL , DABA SHJ AJMAN |  |  | COMPLETED | WORK COMPLETED
2026-01-26 |  | 120260782 | PPM | 37 | AMC | AMAZON | DXB 3 | DXB | Q1 | ABID | RANJITH, SHAHABUDDIN | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-27 | 7:18 | 120260783 | 120260418 | 1 | AMC | AD COOP/DEYAAR | AD MALL | AUH | RAK SYSTEM FAN NOT WORKING | TROVEE | OLIVER/RANDOLP/FROILEN | 14:34 | 16:17 | FOUND FAN MOTORS ARE SHORTED THERE HAVE WINDING FANS /CHANGED FAN MOTORS NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-27 | 9:06 | 120260784 | 120260419 | 1 | AMC | AD COOP/DEYAAR | MADINAT ZAYED | AUH | FREEZER NO 1 UNUSUAL SOUND | OLIVER |  | 9:20 | 10:25 | FOUND OUT PLASTIC STUCK AT THE FAN MOTOR AFTER REMOVE PLASTIC WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-27 | 9:06 | 120260785 | 120260420 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | FROZEN CHICKEN CHILLER NOT WORKING | TROVEE | RANDOLP | 9:45 | 10:10 | CHECKED THE FREEZER WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-27 | 7:20 | 120260786 | 120260421 | 2 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | MILK CHILLER NOT COOLING | SHAFI | MUSTAFA | 10:00 | 11:00 | FOUND COMPRESSOR NOT WORKING NEED REPLACE | NEED:- COPRESSOR-1 NOS 6.5 HP, CONTROL PANNEL-1, FILTER DRIER EK305S- 1NOS, R 22 2 NOS |  | ATTENDED | NEED MATERIAL
2026-01-27 | 8:20 | 120260787 | 120260422 | 1 | AMC | LULU | DHAID | SHJ | FREEZER COLD ROOM TEMP ISSUE. | AHSAN |  | 10:50 | 13:00 | FOUND OUT EVAPORATOR FAN MOTOR NOT WORKING THERE IS NOT FIXING KVR NOW TEMP IS NORMAL | NEED:- NTC SENSOR -1 NOS, KVR CRO-6 0/60 -1NOS, 404 GAS-1NOS, 3/8 FILTER DRIERSD-1NOS,DOOR LOCK -1NOS |  | ATTENDED | NEED MATERIAL
2026-01-27 | 10:04 | 120260788 | 120260423 | 1 | AMC | LULU | AL RAFFA | DXB | CHILLER HIGH TEMP.ISSUE | MUTHUKUMAR | SHABIB | 12:30 | 16:00 | CHECKED THE LEAK BUT LEAK NOT FOUND RELEASED THE OLD GAS SYSTEM VACCUM AFTER GAS CHARED NOW SYSTEM IS WORKING NORMAL | USED:- R 600 GAS BY TD |  | COMPLETED | WORK COMPLETED
2026-01-27 | 9:57 | 120260789 | 120260424 | 1 | WTY | ADNOC | 448 | AUH | WATER LEAK FROM CHILLER CABINET | RANDOLPH |  | 10:40 | 11:14 | FIXED THE DRAIN HOSE PROPERLY |  |  | COMPLETED | WORK COMPLETED
2026-01-27 | 7:58 | 120260790 | 7100293768 | 1 | AMC | ENOC | 1205 | AJM | OPEN CHILLER NOT WORKING | AHSAN | SELVAN | 14:30 | 17:00 | FOUND ICE FORMATION AFTER CHECK ISSUE FAN MOTOR DAMAGE NOW UNIT RUNNING NORMAL | USED:- FAN MOTOR 5W-2NOS |  | COMPLETED | WORK COMPLETED
2026-01-27 | 8:24 | 120260791 |  | 0 | AMC | ENOC | 95 | DXB | OPEN CHILLER NO 1 TRMP -5 | MOHAMMED |  | 13:30 | 14:05 | CHILLER IS WORKING NORMAL NEED TO CHANGE THERMOMETER | NEED :- DISPLAY THERMOMETER- 1NOS |  | ATTENDED | NEED MATERIAL
2026-01-27 | 10:08 | 120260792 |  | 0 | AMC | ENOC | 1161 | SHJ | PRONTO FREEZER TEMP ISSUE. | SABITH ALI |  | 12:50 | 14:00 | FOUND ICE FORMATION AFTER REMOVE ICE RESET UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-27 | 10:19 | 120260793 | 120260425 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER NOISE ISSUE(CH-18) | SABITH ALI |  | 10:50 | 11:25 | FOUND CONDENSER FAN MOTOR TOUCHING IN THE BOADY AFTER RE FITTING NOW NORMAL SOUND |  |  | COMPLETED | WORK COMPLETED
2026-01-27 | 9:00 | 120260794 | 120260405 | 2 | AMC | BADIA FARMS | AL QUOZ | DXB | ZONE 3 CHILLER NOT WORKING | MOHAMMED | MUTHUKUMAR/SHABIB | 10:00 | 11:45 | FOUND LP CUT OFF LESS GAS AFTER CHARGING GAS NOW SYSTEM WORKING GOOD | USED 134 GAS BROM STORE | NEED TO REPLACE PIPE LINE | COMPLETED | WORK COMPLETED
2026-01-27 | 11:00 | 120260795 | 120260407 | 3 | AMC | NESTO | KARAMA | DXB | BUTCHERY CHILLER AND FISHERY CHILLER DISPLAY CHECK | SHAFI | MUSTAFA | 11:30 | 14:00 | CHECKED THE BUTCHERY SECTION COLD ROOM /AFTER CHANGE CONTACTOR BACK TO NORMAL | USED: LC1D12- 2NOS |  | COMPLETED | WORK COMPLETED
2026-01-27 | 12:17 | 120260796 | 120260426 | 2 | AMC | ANSAR | KARAMA | DXB | WATER LEAK FROM FREEZER | MOHAMMED | MUTHUKUMAR/SHABIB | 16:30 | 17:50 | NEED TO REFIXING INSULLATION | NEED :- INSULATION 1 1/8X3/4 - 1NOS, BASION KIT-1NOS, FOAM TAPE-1NOS, COOLING FAN 80X80-4NOS,1.5MM X 3 CORE WIRE-15 MTR,BLACK TAP -2 INCH- 4 NOS. |  | ATTENDED | NEED MATERIAL
2026-01-27 | 12:39 | 120260797 | 120260427 | 1 | AMC | LULU | OLIVE TOWER | AUH | EATER LEAKAGE IN LABAN UP CHILLER | TROVEE | OLIVER/RANDOLP/FROILEN | 13:12 | 13:35 | VACCUM THE DRAIN DRAY OF MILK AND LABAN CHILLER NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-27 | 13:02 | 120260798 | 120260428 | 2 | AMC | NESTO | AL FAHIDI | DXB | ICE FORMATION | SHAFI | MUSTAFA | 15:00 | 16:30 | NEED TO REPLACE DIXCEL CONTROLLER SENSOR | NEED:- DIXEL CONTROLER -1NOS,SENSOR-2NOS,CONTECTOR-1NOS |  | ATTENDED | NEED MATERIAL
2026-01-27 | 9:00 | 120260799 | 120260429 | 1 | AMC | NESTO | AL AIN | AL AIN | COLD ROOM TEMP. ISSUE | TALIB |  | 9:15 | 13:30 | FOUND SENSOR IS NOT WORKING PROPERLY AFTER CHANGING SENSOR NOW STORS ARE NORMAL TEMP. | USED:- NTC SENSOR - 1NOS |  | COMPLETED | WORK COMPLETED
2026-01-27 | 14:53 | 120260800 | 120260430 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | FROZEN VEGETABLE FREEZER TEMP ISSUE | TROVEE | OLIVER/RANDOLP/FROILEN | 16:38 | 17:17 | THERE IS DEFFECTED CONTACTOR AND OVER LOAD | NEED:- LCID25 -1NOS, OVERLOAD LRD14- 1NOS. |  | ATTENDED | NEED MATERIAL
2026-01-27 | 11:00 | 120260801 | 120260407 | 3 | AMC | NESTO | KARAMA | DXB | BUTCHERY CHILLER AND FISHERY CHILLER DISPLAY CHECK | SHAFI | MUSTAFA | 11:30 | 14:00 | FISHERY SECTION COLD ROOM CONTROLER DEFECTED | NEED: EKC 302D -1 NOS , SENSOR- 2NOS |  | ATTENDED | NEED MATERIAL
2026-01-27 | 15:21 | 120260802 | 120260431 | 1 | AMC | ADNOC | 384 | DXB | FREEZER CABINET NOT WORKING PROPERLY | SADAM | ZALAUDIN | 20:00 | 21:20 | CONDENSOR FULL OF DUST/AFTER CLEANING DUST NOW SYSTEM NORMAL WORKING |  |  | COMPLETED | WORK COMPLETED
2026-01-27 | 17:30 | 120260803 | 120260432 | 1 | AMC | CAREEM | ARJAN | DXB | CHILLER TEMP ISSUE. | SADAM | ZALAUDIN | 19:00 | 19:40 | AFTER WE FIXED THE SENSOR CORRECTLY NOW SYSTEM IS NORMAL WORKING |  |  | COMPLETED | WORK COMPLETED
2026-01-27 | 23:15 | 120260804 | 120260433 | 3 | AMC | AD COOP/DEYAAR | SE 13 | AUH | ICE CREAMFREEZER DEFROST FROM LONG TIME | [7 empty] | ATTENDED | ATTENDED ON 28/1/2026
2026-01-27 | 9.44.00 PM | 120260805 | 120260434 | 1 | AMC | NESTO | FUJAIRAH MALL | FUJ | FREEZER SOUND ISSUE | RACEL |  | 23:32 | 2:05 | REMOVE ICE FORMATION UNIT NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-27 |  | 120260806 | PPM | 37 | AMC | PHD | ABU DHABI | AUH | Q3 PPM FINISHED | FROILAN | [6 empty] | COMPLETED | WORK COMPLETED
2026-01-27 |  | 120260807 | PPM | 37 | AMC | CAREEM | JVT | DXB | Q 1 PPM FINISHED | SADAM | ZALAUDIN | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-27 |  | 120260808 | PPM | 37 | AMC | NESTO | AL AIN | AL AIN | CABINET INDOOR SERVICE | TALIB | [6 empty] | COMPLETED | WORK COMPLETED
2026-01-27 | 11:00 | 120260809 | 7100293927 | 2 | AMC | ENOC | 1019 | DXB | WALKIN CHILLER LIGHT NOT WORKING | SHAFI | MUSTAFA | 17:40 | 17:55 | NEED TO REPLACE LIGHT 4 FEET | NEED:- 4 FEET LIGHT - 1NOS |  | ATTENDED | ATTEIND ON 5/2/2025
2026-01-27 | 11:00 | 120260810 | 7100293908 | 1 | AMC | ENOC | 1007 | DXB | PRONTO BED FREEZER NOT WORKING. | RACEL | BIJU | 20:16 | 21:31 | BURNED WIRE NO ELECTRIC SUPPLY /AFTER FIXING WIRE WORKING NORMAL | USED:- 1 METER 3 CORE CABLE WIRE 2.5MM |  | COMPLETED | WORK COMPLETED
2026-01-27 | 21:00 | 120260811 |  | 0 | AMC | ENOC | 412 | RAK | OPEN CHILLER INSTALATION | DENNIS | BIJU/SHAHABUDIN/TALHA | 23:00 | 3:40 | OPEN CHILLER INSTALED /NEED:- PRICE RAIL FOR CHILLER - 8 NOS | NEED:- PRICE RAIL FOR CHILLER - 8 NOS |  | ATTENDED | NEED MATERIAL
2026-01-27 | 21:00 | 120260812 | 120260435 | 2 | WTY | PASONS | FUJAIRAH | FUJ | COMPROSSER INSTALATION | SABITH ALI | SELVAN | 20:00 | 24:30 | REPLACED COMPRESSOR | USED:- COMPRESSER-1 NOS(WTY),CONTACTER 25AMP-1NOS, OVERLOADER-1NOS,FILTER DRIER3/8-1NOS, R22-1NOS, COPPER PIPE- 7/8- 1/2 METER, 7/8 ELBOW-1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-27 | 12:33 | 120260813 | 7100293769 | 2 | AMC | ENOC | 1444 |  | CHILLER LIGHT HOLDER DAMAGE | [7 empty] | ATTENDED | ATTENDED ON 3/2/2026
2026-01-27 | 12:33 | 120260814 | 7100293849 | 1 | AMC | ENOC | 1032 |  | OPEN CHILLER SHELF FOR REPAINTING | SARAVANAN | [6 empty] | COMPLETED
2026-01-27 | 12:33 | 120260815 | 7100293944 | 3 | AMC | ENOC | 509 |  | OPEN CHILLER LIGHT NOT WORKING | SABITH ALI | [6 empty] | ATTENDED | ATTENDED ON 29/1/2026
2026-01-27 | 8:00:00PM | 120260816 | MINA PROJECT | 9 | AMC | AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | ROGER | GOVIND, SUDHEESH, ABIJITH | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-27 |  | 120260817 | DRIVING | 27 |  |  |  |  | DRIVING | WILSON |  | 7:30 | 18:45 | DUBAI TO AJMAN, AJMAN INDUSTREAL , SHJ AJMAN |  |  | COMPLETED | WORK COMPLETED
2026-01-27 |  | 120260818 | PPM | 37 | AMC | AMAZON | DXB 3 | DXB | Q1 | ABID | RANJITH, SHAHABUDDIN | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-28 | 8:46 | 120260819 | 120260436 | 1 | AMC | AD COOP/DEYAAR | ABU DHABI | AUH | WATER LEAK FROM C9 CHILLER IN FROZEN SECTION | OLIVER | FROILAN | 11:20 | 13:00 | FONUD WATER LINE ALREADY DONE BY BRANCH MAINTANCE TEAM |  |  | COMPLETED | WORK COMPLETED
2026-01-28 | 9:33 | 120260820 | 120260437 | 2 | AMC | AD COOP/DEYAAR | ABU DHABI | AUH | ICE MAKER FISHERY SECTION NOT WORKING | OLIVER | FROILAN | 11:20 | 13:00 | FOUND MICRI SWITCH NOT FUNTION | NEED:- MICRO SWITCH D43X - 2 NOS |  | ATTENDED | NEED MATERIAL
2026-01-28 | 8:46 | 120260821 | 120260438 | 1 | AMC | BAQER MOHEBI | AL NAHDA | SHJ | BAKERY CHILLER NOT WORKING NO 18 | RACEL | BIJU | 19:05 | 19:55 | RECTIFY THE ROCKER SWTICH NOT WORKING / UNIT NOW WORKING | NEED:- ROCKER SWITCH - 2PCS |  | ATTENDED | NEED MATERIAL
2026-01-28 | 7:53 | 120260822 | 120260439 | 1 | AMC | ADNOC | 634 | SHJ | WATER LEAK FROM FILTER | AHSAN | SELVAN | 13:20 | 13:35 | AFTER CUT PIPE EDGE AND FIX PROPERLY |  |  | COMPLETED | WORK COMPLETED
2026-01-28 | 9:48 | 120260823 | 120260440 | 1 | AMC | NESTO | AJF | AJM | DELI CHILLER TEMP ISSUE. | AHSAN | SELVAN | 10:50 | 11:40 | CHARGED GAS FROM STORE /NEED TO LEAK TEST | NEED LEAK TEST IN THIS SYSTEM |  | ATTENDED | RESCHEDULE
2026-01-28 | 6:11 | 120260824 | 5000218243 | 1 | AMC | ENOC | 1135 | SHJ | BED FREEZER TEMP. | AHSAN | SELVAN | 9:00 | 10:20 | CHANGED THE SETTINGS NOW TEMP RECHED SET POINT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-28 | 9:48 | 120260825 |  | 0 | AMC | ENOC | 1063 | DXB | BED FREEZER GASKET | MUSTAFA |  | 14:10 | 14:55 | BED FREEZER GASKET CHANGED | USED:- GASKET |  | COMPLETED | WORK COMPLETED
2026-01-28 | 9:48 | 120260826 | 7100291988 | 3 | AMC | ENOC | 1085 | DXB | WALKIN CHILLER PVC CURTIN FIXING | SARAVANAN | SHABIB | 11:00 | 11:15 | CHANGED NEW PVC CURTIN |  |  | COMPLETED | WORK COMPLETED
2026-01-28 | 11:16 | 120260827 | 120260441 | 1 | AMC | AD COOP/DEYAAR | MBZ | AUH | WATER LEAK IN CHILLER | TROVEE | RANDOLP | 14:24 | 14:55 | AFTER FLUSHING DRAIN LINE NOW NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-28 | 11:16 | 120260828 | 7100293001 | 2 | AMC | ENOC | 1079 | DXB | CHILLER DOOR HANDLE BROKEN | SARAVANAN |  | 13:15 | 14:30 | FIXED DOOR HANDEL | USED:-DOOR HANDEL |  | COMPLETED | WORK COMPLETED
2026-01-28 | 11:16 | 120260829 | 7100291644 | 3 | AMC | ENOC | 1022 | DXB | NEED TO FIX PVC CURTAIN | SARAVANAN | SHABIB | 11:50 | 12:35 | FIXED PVC CURRTIN | USED :- PVC CURTINE |  | COMPLETED | WORK COMPLETED
2026-01-28 | 13:13 | 120260830 | 120260442 | 1 | AMC | ENOC | 1005 | DXB | WALK IN CHILLER HIHG TEMP. | SABITH ALI |  | 18:30 | 19:45 | AFTER LOW GAS ICE FORMATION IN EVAPORATOR /AFTER GAS CHARGE NOW SYSTEM IS NORMAL | USED:- 404 GAS - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-28 | 12:15 | 120260831 | 120260443 | 1 | AMC | GOURMET | 1004 | AUH | FREEZER AND CHILLER TEMP. ISSUE | OLIVER | FROILAN | 13:15 | 14:40 | FIND THE ISSUE FAN MOTOR NOT WORKING | NEED:- FAN MOTOR 16W 220V - 1NOS |  | ATTENDED | NEED MATERIAL
2026-01-28 | 16:10 | 120260832 | 120260444 | 2 | AMC | HOP | JEBAL ALI | DXB | PACKING ROOM AC NOT WORKING ALSO NEW DOOR HANDLE NOT WORKING | MOHAMMED | [6 empty] | ATTENDED | ATTENDED ON 29/1/2026
2026-01-28 | 16:41 | 120260833 | 5000218336 | 2 | AMC | ENOC | 1125 | SHJ | OPEN CHILLER HIGH TEMP | AHSAN | [6 empty] | ATTENDED | ATTENDED ON 29/1/2026
2026-01-28 | 17:30 | 120260834 | 120260445 | 2 | AMC | GRANDIOSE | WASL VILLAGE | DXB | PORK SECTION TEMP ISSUE | RACEL | BIJU | 20:45 | 22:55 | STUCK-UP MECHANICAL OF COMPRESSOR | NEED:- ADZ36VBBMTS FULL SET -1 NOS, FILTER DRIER 3/8-1 NOS,R404-1CYLD,NITROGEN-1CYLD,141B-1CYLD,BLUE ROD-4NOS,BRAZING ROD-8NOS,ORIFACE NO 1 - 1NOS. |  | ATTENDED | ATTENDED ON 3/2/2026
2026-01-28 | 17:30 | 120260835 | 120260446 | 1 | AMC | GOURMET | AL GHURAIR | DXB | COLD ROOM TEMP. ISSUE | SADAM | ZALAUDIN |  |  | CANT ATTENT COMPLENT WITHOUT PERMIT |  |  | NOT ATTENDED | RESCHEDULE
2026-01-28 | 23:15 | 120260836 | 120260433 | 3 | AMC | AD COOP/DEYAAR | SE 13 | AUH | ICE CREAMFREEZER DEFROST FROM LONG TIME | TROVEE | RANDOLP/OVILER | 9:00 | 10:53 | LESS GAS NO LEAK FOUND IN ALL FREEZER | NEED:- R 404A - 7 CYLD |  | ATTENDED | NEED MATERIAL
2026-01-28 | 18:51 | 120260837 | 120260447 | 2 | AMC | LULU | NUAIMIA | AJM | VEG CHILLER TEMP ISSUE. | [7 empty] | ATTENDED | ATTENDED ON 29/1/2026
2026-01-28 | 18:53 | 120260838 | 120260448 | 1 | AMC | TCS | UMS | DXB | ICE FORMATION IN DEI CHILLER AND MEAT BACKSTORE HIGH TEMP. | SADAM | ZALAUDIN | 21:00 | 24:00 | DELI CHILLER FAN MOTOR STUCK AFTER REPLACE WORKING NORMAL | USED:- BOX FAN 80x 80 - 1NOS |  | COMPLETED | WORK COMPLETED
2026-01-28 | 6:26 | 120260839 | 120260358 | 2 | AMC | CAREEM | AL SAFA | DXB | CHILLER HIGH TEMP. | MUTHUKUMAR | TALHA |  |  | CHANGED COPMRESSOR | USED:- COMPRESSOR EMBRACO NJ9238GK -1NOS,404 -1CYILS,NITROGEN SMALL-1NOS,1/4 FILTER DRIER SD TYPE,CHANRGING PIN-1NOS,BLUE ROD-2 STICK,COPPER ROD -2NOS |  | COMPLETED | WORK COMPLETED
2026-01-28 | 9:10:00PM | 120260840 | 120260449 | 2 | AMC | GOURMET | 1004 | AUH | FREEZER NOISE ISSUE | [7 empty] | ATTENDED | ATTENDED ON 29/1/2026
2026-01-28 | 16:00 | 120260841 | 120260421 | 2 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | MILK AND JUICE CHILLER NOT WORKING | SHAFI | MUSTAFA/AHSAN/SABITH/SELVEN | 17:00 | 23:00 | CHANGED COPMRESSOR | USED:- COPRESSOR-1 NOS 6.5 HP, CONTROL PANNEL 7HP-1, FILTER DRIER EK305S 5/8- 1NOS, R 22 2 NOS,CABLE 1.5X5CR - 3MTR,CABLE CONDUIT GI FLEXIBLE-3 MTR. |  | COMPLETED | WORK COMPLETED
2026-01-28 |  | 120260842 | PPM | 37 | AMC | AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | ROGER | GOVIND, SUDHEESH, ABIJITH |  |  | WORK COMPLETED |  |  | COMPLETED | WORK COMPLETED
2026-01-28 | 18:30 | 120260843 | 120260433 | 3 | AMC | AD COOP/DEYAAR | SE 13 | AUH | GAS CHARGED | RANDOLPH |  | 19:24 | 22:20 | AFTER GAS CHARGED NOW TEMP. NORMAL | USED:- 404 7NOS FROM BRANCH |  | COMPLETED | WORK COMPLETED
2026-01-28 |  | 120260844 | DRIVING | 27 | AMC |  |  | DXB | DRIVING | MOHAMMED |  | 8:00 | 19:00 | CAR REPAIR,COMPRESOR COLLECTION |  |  | COMPLETED | WORK COMPLETED
2026-01-28 |  | 120260845 | PPM | 37 | AMC | AMAZON | DXB 3 | DXB | PPM | ABID | RANJITH, SHAHABUDDIN | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-28 |  | 120260846 | DRIVING | 27 | AMC |  |  | DXB | DRIVING | WILSON |  | 7:30 | 20:20 | SHJ,AJMAN,DXB |  |  | COMPLETED | WORK COMPLETED
2026-01-28 | 20:23 | 120260847 | 120260477 | 1 | AMC | NESTO | KARAMA | DXB | BAKERY DISPLAY TEMP ISSUE. | SADAM | ZALAUDIN | 1:30 | 3:00 | COMPRESOR DEFECTED | NEED : COMPRESSOR NEK6210GF , 404 GAS |  | ATTENDED | NEED MATERIAL
2026-01-29 | 9:15 | 120260848 | 120260450 | 1 | AMC | ADNOC | 917 | AUH | FREEZER TEMP ISSUE. ICE CREAM TEMP ISSUE. | RANDOLPH | TROVEE | 10:00 | 11:00 | AFTER CLEAN THE CONDENSOR AND CHARGE 404 GAS NOW UNIT IS NORMAL WORKING | USED: 404 A |  | COMPLETED | WORK COMPLETED
2026-01-29 | 8:00 | 120260849 | 120260444 | 2 | AMC | HOP | JEBAL ALI | DXB | PACKING ROOM AC NOT WORKING ALSO NEW DOOR HANDLE NOT WORKING | MOHAMMED | SHABIB | 7:25 | 11:00 | AFTER REMOVE ICE FORMATION FROM EVAPORATOR UNIT IS WORKING NORMAL/BUT NEED TO CHANGE H/P KP10 | NEED:- H/P SWITCH KP 10-1 NOS, H/PHOSE 1/4 X 1/4 - 1 NOS, BRASS UNION 1/4-1NOS. |  | ATTENDED | NEED MATERIAL
2026-01-29 | 8:00 | 120260850 | 120260449 | 2 | AMC | GOURMET | 1004 | AUH | FREEZER NOISE ISSUE | RANDOLPH | TROVEE | 8:00 | 9:00 | FOUND OUT MAIN WIRE TOUCH ON THE FAN MOTOR AND ANSO BUSTED LED LIGHT | USE:- LED LIGHT FROM BRANCH STOCK |  | COMPLETED | WORK COMPLETED
2026-01-29 | 7:50 | 120260851 | 120260451 | 1 | AMC | BAQER MOHEBI | AL NADHA | DXB | SOUND FROM CHEESE CHILLER | VIGNESH |  | 9:05 | 12:00 | CHANGED THE FAN MOTOR WORKING NOW NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-29 | 8:00 | 120260852 | 120260447 | 2 | AMC | LULU | NUAIMIA | AJM | VEG CHILLER TEMP ISSUE. | AHSAN |  | 9:00 | 11:00 | FOUND DRAIN PAN DAMAGE NEED TO CHANGE | NEED:- WATER DRAIN PAN - 1NOS - 21 X 43 X 45.5 CM |  | ATTENDED | NEED MATERIAL
2026-01-29 | 9:53 | 120260853 | 120260452 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | CHEESE COLD ROOM TEMP ISSUE. | VIGNESH | AHSAN | 12:20 | 17:30 | FOUND SUCTION PIPE LEAK AFTER RECTIFY CHILLER WORKING NORMAL | USED:404 GAS-1 NOS, COPPER PIPE - 5/8 - 1 MTR |  | COMPLETED | WORK COMPLETED
2026-01-29 | 10:40 | 120260854 | 120260453 | 1 | AMC | BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER LIGHT NOT WORKING | VIGNESH | AHSAN | 12:20 | 17:30 | BAKERY CHILLER LIGHTS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-29 | 10:58 | 120260855 | 120260454 | 1 | AMC | NESTO | KARAMA | DXB | WATER LEAK FROM VEGETABLE CHILLER PIPE LINE IN PARKING AREA | MOHAMMED | SHABIB | 16:00 | 16:45 | SYSTEM PIPE LINE INSULATION DAMAGE NEED TO REPLACE THE INSULATION | NEED:- PIPE INSULATION - 1 1/8 X 3/4 - 4 NOS, BAISON KIT-1 NOS, BLACK TAP 2INCH - 4 NOS, FOAM TAP- 4 NOS, SPRAY FOAM-3 NOS. |  | ATTENDED | NEED MATERIAL
2026-01-29 | 8:40 | 120260856 | 120260455 | 1 | AMC | TCS | UMS | DXB | TRIPPING UNIT AND WEIGHING SCALE | MOHAMMED | SHABIB | 11:30 | 14:00 | DELI SECTION CHILLER TRIPPING CHANGED THE BOX FAN NOW SYSTEM WORKING NORMAL NEED TO CHANGE DRAIN TRAY HEATER -1 NOS | NEED :- DRAIN TRAY HEATER - 1NOS |  | ATTENDED | NEED MATERIAL
2026-01-29 | 11:55 | 120260857 | 120260456 | 1 | AMC | NESTO | AL AIN | AL AIN | FREEZER COLD ROOM TEMP.ISSUE | TALIB |  | 13:00 | 15:25 | FOUND LIMIT SWITCH PROBLEM /AFTER FIXING PROPER LIMIT SWITCH NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-29 | 12:51:PM | 120260858 | 120260457 | 2 | AMC | NESTO | AJC | AJM | FISH SECTION BED FREEZER TEMP.ISSUE | SABITH ALI |  | 16:00 | 18:20 | REMOVED THE CONDENSOR COIL DUST AND TRIPP ON NOW SYSTEM IS WORKING NORMAL | USED:- CONDENSER FAN 5W - 1NOS |  | COMPLETED | WORK COMPLETED
2026-01-29 | 9:00 | 120260859 | PPM | 37 | AMC | WESTLAND | AL AIN | AL AIN | OBSERVATION ALL CHILLER UNITS | TALIB |  | 9:45 | 12:25 | OBSERVATION ALL CHILLER UNITS |  |  | COMPLETED | WORK COMPLETED
2026-01-29 | 9:00 | 120260860 | 120260458 | 1 | WTY | PASONS | FUJAIRAH | FUJ | CONDENSSOR FAN MOTOR CHANGE - 1 NOS 350MM | SABITH ALI |  | 10:15 | 11:45 | CONDENSSOR FAN MOTOR CHANGE - 1 NOS 350MM |  |  | COMPLETED | WORK COMPLETED
2026-01-29 | 7:50 | 120260861 | 120260459 | 1 | AMC | BAQER MOHEBI | AL NADHA | DXB | COLD ROOM COMPRESSOR SOUND | VIGNESH |  | 9:50 | 12:00 | MECHANICAL SOUND SO NEED TO REPLACE COMPRESSOR | NEED : COMPRESSOR TAG4546T - 1NOS, FILTER DRIER 163-1 NOS, CONDENSER FAN 350MM - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-01-29 | 12:51:PM | 120260862 | 120260457 | 2 | AMC | NESTO | AJC | AJM | COLD ROOM LIGHT NOT WORKING | SABITH ALI |  | 16:00 | 18:20 | CHANGED LIGHT | USED:- 4 FEET LEDTUB-2 NOS. |  | COMPLETED | WORK COMPLETED
2026-01-29 | 14:52 | 120260863 | 7100293944 | 3 | AMC | ENOC | 509 | FUJ | OPEN CHILLER LIGHT NOT WORKING | SABITH ALI |  | 12:15 | 13:05 | OPEN CHILLER LIGHT IS DAMAGE NEED TO REPLACE | NEED : TUBELIGHT-1 NOS |  | ATTENDED | NEED MATERIAL
2026-01-29 | 14:52 | 120260864 | 7100294102 | 1 | AMC | ENOC | 509 | FUJ | W/C UNIT SHEET DAMAGE | SABITH ALI |  | 12:15 | 13:05 | SCREW ARE BROKEN /AFTER NEW SCREW THIGHTED NOW NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-29 | 15:10 | 120260865 | 120260460 | 1 | AMC | NESTO | AJE | AJM | FREEZERN NOT WORKING | RACEL | BIJU | 19:28 | 20:36 | AFTER CLEANING CONDENSER SYSTEM BACK TO NORMAL WORKING |  |  | COMPLETED | WORK COMPLETED
2026-01-29 | 9:00 | 120260866 | 5000218336 | 2 | AMC | ENOC | 1125 | SHJ | OPEN CHILLER HIGH TEMP | AHSAN |  | 12:40 | 13:15 | NOW CHECK THE UNIT PROBLEM IS COMPRESSOR DAMAGE | NEED: COMPRESSOR ZX21KCE-TFD-558 -1NOS,404 GAS-1NOS,1/2FILTER DRIER,BLUE ROD - 1NOS, CONDACTOR 18 AMP - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-01-29 | 16:18 | 120260867 | 120260461 | 1 | AMC | BAQER MOHEBI | SATWA | DXB | CHILLER 4 FEET WARM WHITE NOT WORKING | SADAM | ZALAUDIN | 21:50 | 1:25 | LAMP FUSE NEED TO BE REPLACE | NEED:- T5 LED WARM LIGHT FULL FITTING-01,4 FEET TE LED TUBE-03 NOS,2 FEET T8 LED TUBE-02NOS |  | COMPLETED | WORK COMPLETED
2026-01-29 | 16:35 | 120260868 | 120260462 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | F1 WALK IN FREEZER NO POWER | RANDOLPH | TROVEE | 18:50 | 20:00 | AFTER CHANGING FUSE NOW SYSTEM IS WORKING NORMAL | USED:- LED LIGHT AND FUSE FROM BRANCH STORE |  | COMPLETED | WORK COMPLETED
2026-01-29 | 11:00 | 120260869 | 120260390 | 2 | AMC | TCS | ROVE TRADE CENTER | DXB | CHILLERS HIGH TEMP.ISSUE. | SARAVANAN |  | 13:10 | 14:25 | CH-2 CHILLER CONTROLLER CHANGED NOW WORKING NORMAL NEED PT 1000 SENSOR | USED:- CONTROLLER IPC DANFOSS 202D - 1NOS, CONDENSSOR FAN 25W-1NOS/NEED : PT 1000 SENSOR -2NOS |  | ATTENDED | NEED MATERIAL
2026-01-29 | 17:00 | 120260870 | 120260463 | 1 | AMC | GRANDIOSE | BIN SHABIB MALL | DXB | FREEZER ISSUE DOOR , MILK YOUGUT CHILLER SLIDING | SADAM | ZALAUDIN | 18:45 | 20:45 | FREEZER DOOR HINGES NEED TO REPLACE, MILK CHILLER DOOR LOCK | NEED:- DOOR HINGES - 1 SET |  | ATTENDED | NEED MATERIAL
2026-01-29 | 15:45 | 120260871 |  | 0 | AMC | ENOC | 4009 | DXB | CHILLER WATER LEAK | SABITH ALI | [6 empty] | ATTENDED | ATTENDED ON 30/1/2026
2026-01-29 | 18:00 | 120260872 | 7100294297 | 2 | AMC | ENOC | 1126 | SHJ | VERTICAL FREEZER HGH TEMP. | RACEL |  | 22:11 | 1:35 | FOUND LEAK FROM PRIMARY COIL NEED TO CHANGE COIL AND COMPRESSOR | NEED:- COMPRESSOR NEU21684 -1NOS, FILTER DRIER-1/4 - 1NOS,R290- 1NOS,NITROGEN-1NOS,2METER COPPER 1/4TUBE,BLUE ROD-4STICK,BRAZING ROD-3STICK,141B CYLD. |  | ATTENDED | NEED MATERIAL
2026-01-29 | 17:15 | 120260873 | 120260352 | 2 | AMC | GOURMET | 1004 | AUH | PORKSECTION FREEZER TEMP ISSUE | OLIVER | FROILAN | 18:35 | 22:35 | FOUND UNIT COMPRESSOR DEFFECTIVE NEED TO CHANGE | USED:- COMPRESSOR CAJ2446Z FLARE TYPE-1NOS, FILTER DRIER 3/8 SD-1NOS, GAS 404-1CYLD,BREZING ROD -2 STICK. |  | COMPLETED | WORK COMPLETED
2026-01-29 |  | 120260874 | PPM | 37 | AMC | AMAZON | DXB 3 | DXB | PPM | ABID | RANJITH |  |  | PPM |  |  | COMPLETED | WORK COMPLETED
2026-01-29 |  | 120260875 | DRIVING | 27 | AMC |  |  |  | DRIVING | WILSON |  | 9:00 | 20:00 | SHARJAH ,AJAMAN, DXB |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 5:26 | 120260876 | 120260464 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | CHILLER B 22 MAKING SOUND | RANDOLPH | TROVEE | 8:33 | 10:35 | VACCUM THE DRAIN FROM B 22 CHILLER |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 7:40 | 120260877 | 120260465 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | FREEZER NOT WORKING | RANDOLPH | TROVEE | 8:33 | 10:35 | CHANGED THE FAN MOTOR WORKING NORMAL | USED :- CONDENSOR FAN MOTOR -BY BRANCH |  | COMPLETED | WORK COMPLETED
2026-01-30 | 7:44 | 120260878 | 120260466 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | F&V FREEZER NOT WORKING | RANDOLPH | TROVEE | 8:33 | 10:35 | AFTER REMOVING ICE FORMATION SYATEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 8:37 | 120260879 | 120260467 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE ICE NOT FALLING | IN HOUSE TEAM |  |  |  | INHOUSE TEAM STARTED THE UNIT |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 8:48 | 120260880 | 120260468 | 1 | AMC | AD COOP/DEYAAR | MEGAMART AL NADHA | SHJ | CHILLER NO 4 TRIPPING UNIT | VIGNESH |  | 9:50 | 12:10 | CHECKED THE ISSUE LIGHT ARE SHORT NEE TO CHANGE LIGHT | NEED:- LED 4FEET LIGHT - 2NOS |  | ATTENDED | NEED MATERIAL
2026-01-30 | 11:11 | 120260881 | 120260469 | 1 | AMC | ANSAR | KARAMA | DXB | MEAT CHILLER TEMP.ISSUE | SABITH ALI |  | 15:05 | 15:25 | UNIT IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 11:34 | 120260882 | 120260470 | 1 | AMC | CAREEM | JVC PLAZA | DXB | FREEZER TEMP.ISSUE | SARAVANAN |  | 13:00 | 17:00 | AFTER SYSTEM VACUM AND RECTIFY COMPLENT NOW SYSTEM NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 9:16 | 120260883 |  | 0 | AMC | ENOC | 4009 | DXB | CHILLER WATER LEAK | SABITH ALI |  | 11:03 | 13:50 | AFTER ADJUST HEATER TIMING NOW UNIT IS NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 9:16 | 120260884 | 120260471 | 1 | AMC | AL MASA | KIZAD | AUH | 8 COLD ROOM NEED TO BE START | OLIVER | FROILAN | 14:55 | 18:00 | COLD ROOM TEMP SET NOW BUT DOORS OPEN BY LOADING TIME AND FLOOR CLEANING TIME NOT COOLING ROOM AND AUTOMATIC DOORS FOUND NOT WORKING FUNTION |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 11:21 | 120260885 | 120260472 | 1 | AMC | NESTO | AJE | AJM |  | RACEL |  |  |  | AS PER STORE INCHARGE THEY GIVEN SCHEDULE FOR MONDAY NIGHT |  |  | NOT ATTENDED | RESCHEDULE
2026-01-30 | 12:00 | 120260886 | 120260437 | 2 | AMC | AD COOP/DEYAAR | ABU DHABI | AUH | ICE MAKER FISHERY SECTION NOT WORKING | RANDOLPH | TROVEE | 12:33 | 13:24 | COLLECT SWITCH FROM STOR AND FIXED IT | USED:- MICRO SWITCH D43X - 2 NOS BY BRANCH |  | ATTENDED
2026-01-30 | 12:34 | 120260887 | 120260473 | 1 | AMC | BAQER MOHEBI | SATWA | DXB | JICE AND WATER CHILLER WATER LEAK | RACEL |  | 19:32 | 20:46 | CONDENSOR COIL DRAIN PAN HAS LEK AFTER PLUSHING THE DRAIN LINE AND APPLY SILLICON TO THE END WALL CAP NOW THERE IS NO LEAK |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 14:08 | 120260888 | 120260474 | 1 | AMC | GOURMET | 1004 | AUH | FAN SOUND CONDENSOR
2026-01-30 | 14:45 | 120260889 | 120260475 | 1 | AMC | NESTO | FUJEIRAH | FUJ | CHILLER CABINETS TEMP ISSUE | VIGNESH |  | 16:00 | 18:00 | DELI CHILLER FAN MOTOR STUCK AFTER REPLACE WORKING NORMAL | USED:- FAN MOTOR 10W - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-30 |  | 120260890 | 120260476 | 1 | AMC | AMAZON | DXB 5 | DXB | HAMZAT ROOM TEMPURATURE ISSUE | ABID | RANJITH |  |  | REMOVED OLD SENSOR AND REPLACED NEW ONE | USED:TEMP. SENSORE -1NOS BY AMAZON |  | COMPLETED | WORK COMPLETED
2026-01-30 | 11:26 | 120260891 | 7100294180 | 2 | AMC | ENOC | 1061 |  | vertical freezer metal plate need fix | [7 empty] | ATTENDED | ATTENTED ON 31/1/2026
2026-01-30 | 11:26 | 120260892 | 7100294276 | 1 | AMC | ENOC | 1005 |  | Walk in chiller temperature very high | SABITH ALI | [6 empty] | COMPLETED
2026-01-30 | 11:26 | 120260893 | 7100294281 | 2 | AMC | ENOC | 1033 |  | WALK IN FREEZER ICE FORMATION | SADAM | ZALAUDIN | 23:55 | 24:30 | PVC CURTAIN DAMAGE AND NEED TO REPLACE | NEED :- PVC CURTAIN - 2 NOS |  | ATTENDED | ATTENTED ON 1/2/2026
2026-01-30 | 11:26 | 120260894 | 7100294288 | 1 | AMC | ENOC | 1060 |  | London Diary freezer 1 is not working | [7 empty] | NOT ATTENDED | NOT UNDER OUR SCOPE
2026-01-30 | 11:26 | 120260895 | 7100294292 | 1 | AMC | ENOC | 1032 |  | WALK-IN FREEZER | SABITH ALI |  | 16:40 | 17:15 | FOUND ICE FORMATION AND INSPECTED THE DRAIN PIPE SECTION LEAK | AFTER RECTIFAY UNIT IS NORMAL |  | COMPLETED | WORK COMPLETED
2026-01-30 | 11:26 | 120260896 | 7100294380 | 1 | AMC | ENOC | 1079 |  | Rubber gasket | SARAVANAN | SHABEEB | 23:00 | 11:30 | FOUND GASKIT DAMAGE | NEED: CHILLER AND FREEZER DOOR GASKIT NEED TO CHANGE |  | ATTENDED | NEED MATERIAL
2026-01-30 | 11:26 | 120260897 | 7100294463 | 2 | AMC | ENOC | 1031 |  | walk in chiller door cannot close | [7 empty] | ATTENDED | ATTENTED ON 31/1/2026
2026-01-30 | 11:26 | 120260898 | 7100294469 | 1 | AMC | ENOC | 1039 |  | chiller door not closing properly. | SADAM | ZALAUDIN | 22:10 | 23:45 | FIXED THE DOOR ALLIGNMENT NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 11:26 | 120260899 | 7100294470 | 1 | AMC | ENOC | 1039 |  | Ice formation in walk in freezer | SADAM | ZALAUDIN | 22:10 | 23:45 | EVAPORATOR COIL ONE SIDE ONLY ICE FORMATION NEED TO SUTDOWN THE UNIT |  |  | ATTENDED | RESCHEDULE
2026-01-30 | 11:26 | 120260900 | 7100294524 | 1 | AMC | ENOC | 1039 |  | Sandwich chiller having noise | SADAM | ZALAUDIN | 22:10 | 23:45 | EVAPORATORFAN MOTOR CHANGED NOW WORKING NORMAL | USED:- FAN MOTOR 10 W-1NOS |  | COMPLETED | WORK COMPLETED
2026-01-30 | 11:26 | 120260901 | 7100294297 | 2 | AMC | ENOC | 1125 | SHJ | VERTICAL FREEZER HGH TEMP. | AHSAN | SELVAN | 11:30 | 15:55 | FOUND LEAK FROM PRIMARY COIL NEED TO CHANGE COIL AND COMPRESSOR | USED: COMPRESSOR ZX21KCE-TFD-558 -1NOS,404 GAS-1NOS,1/2FILTER DRIER,BLUE ROD - 1NOS, CONDACTOR 18 AMP - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-30 | 19:27 | 120260902 | 120260478 | 2 | AMC | CAREEM | BB3 |  | MOISTURE ISSUE | MOHAMMED | [6 empty] | ATTENDED | ATTENTED ON 31/1/2026
2026-01-30 | 13:00 | 120260903 | 720250972 | 1 | AMC | LULU | DIP | DXB | FREEZER IS NOT WORKING | SHAFI/DENNIS | MUSTAFA | 24:00 | 4:40 | REFIL 10 CYL AND UNIT WORKING NORMAL, COMP#3 VIBRATION ELIMINATOR DAMAGE | USED: VIBRATION ELIMINATOR 1-3/8 35MM L400MM-1 |  | COMPLETED | WORK COMPLETED
2026-01-30 | 13:00 | 120260904 | 1220250318 | 1 | AMC | LULU | DIP | DXB | COMPRESSOR ICE FORMATION | MOHAMMED |  | 24:00 | 4:40 | NEED TO REPLACE SUB COOLING EVP VALVE, ADJUST TRHE SETTING AND WORKING NORMAL | USED: EXP VALVE TE2-1NOS, ORIFICE #05-1NO |  | COMPLETED | WORK COMPLETED
2026-01-30 | 18:00 | 120260905 | 120260479 | 1 | AMC | GRANDIOSE | JUNTION MALL DIP | DXB | CHILLERS NOT WORKING | SHABIB | SADAM | 18:45 | 21:35 | TEMPORARY TURN ON THE SYSTEM BUT NEED TO CHANGE CONTROLLER AND LP SWITCH | NEED : EMERSON CONTROLLER -1NOS , KP 5 LP SWITCH - 1 NOS. |  | ATTENDED | NEED MATERIAL
2026-01-30 | 21:42 | 120260906 | 120260480 | 1 | AMC | LULU | NUAIMIA | SHJ | BUTCHERY CHILLER HIGH TEMP. | RACEL |  | 23:36 | 1:05 | AFTER CLEAN EVAPORATOR NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 0:00 | 120260907 | 120260481 | 1 | AMC | CAREEM | MARINA | DXB | 2 CHILLER NOT WORKING | SADAM | ZALAUDIN | 1:00 | 1:45 | FOUND ELECTRICEL PROBLEM IN POWER SOCKET NEED TO CHECK WITH ELECTICIAN. |  |  | COMPLETED | WORK COMPLETED | NIGHT WORK
2026-01-30 |  | 120260908 | PPM | 37 | AMC | ENOC | 1042 | DXB | Q 4 PPM | MUTHUKUMAR | SHAHABUDIN |  |  | PPM |  |  | COMPLETED | WORK COMPLETED
2026-01-30 |  | 120260909 | PPM | 37 | AMC | ENOC | 1045 | DXB | Q 4 PPM | BIJU | TALHA |  |  | PPM |  |  | COMPLETED | WORK COMPLETED
2026-01-30 | 16:00 | 120260910 | 120260491 | 1 | AMC | AD COOP/DEYAAR | SPAR ADIA C 18 | AUH | DAMAGED GLASS DOOR OF CHILLER | RANDOLPH | TROVEE | 16:55 | 17:05 | NEED TO CHANGE GLASS | NEED : 3 LEFT OPENING GLASS,1 RIGHT OPENING GLASS |  | ATTENDED | NEED MATERIAL
2026-01-30 | 7:00 | 120260911 | DRIVING | 27 | AMC |  |  |  | DRIVING | WILSON |  | 7:05 | 21:30 |  |  |  | COMPLETED | WORK COMPLETED
2026-01-31 | 8:06 | 120260912 |  | 0 | AMC | ENOC | 4016 | DXB | WATER LEAK FROM OPEN CHILLER | SARAVANAN |  | 10:30 | 11:30 | DRAIN LINE PLUSEHD NOW NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-31 | 8:44 | 120260913 |  | 0 | AMC | ENOC | 1071 | DXB | WALKIN CHILLER DOOR HANDEL FIXING | SHAFI | MUSTAFA | 10:15 | 11:15 | REPLACED HANDLE -5 SET | USED:- DOOR HANDEL - 5 NOS |  | COMPLETED | WORK COMPLETED
2026-01-31 | 10:19 | 120260914 | 7100294430 | 1 | AMC | ENOC | 1126 | SHJ | COMPRESSOR NRRD TO BE CHNGE | AHSAN | SELVAN | 11:55 | 19:40 | REPLACED THE COMPRESSOR NOW CHANGE THE PRIMERY COIL ALSO | USED:- COMPRESSOR AND INSTALATION MARIEAS |  | COMPLETED | WORK COMPLETED
2026-01-31 | 10:19 | 120260915 | 7100294463 | 2 | AMC | ENOC | 1031 | DXB | walk in chiller door cannot close | SHAFI | MUSTAFA | 12:00 | 12:50 | FOUND FREEZER DOOR NOT CLOSING B'COZ OF ICE FORMATION/REMOVED THE ICE FORMATION NOW DOOR WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-31 | 11:26 | 120260916 | 7100294180 | 2 | AMC | ENOC | 1061 |  | vertical freezer metal plate need fix | SHAFI | MUSTAFA | 13:20 | 14:00 | FIXED THE SHEET WITH NEW SCREW AND SILICON |  |  | COMPLETED | WORK COMPLETED
2026-01-31 | 13:00 | 120260917 | 120260482 | 1 | AMC | ADNOC | 330 | SHJ | ICE MACHINE NOT WORKING | VIGNESH |  | 13:00 | 15:55 | FOUND INLET PUMP NOT WORKING | USED: WATER INLET PUMP -1 NOS |  | COMPLETED | WORK COMPLETED
2026-01-31 | 19:27 | 120260918 | 120260478 | 2 | AMC | CAREEM | BB3 | DXB | MOISTURE ISSUE | MOHAMMED |  | 9:30 | 10:45 | CLEAN THE MOISTER AND RESET THE DEFROST TIMMER NOW WORKING OK |  |  | COMPLETED | WORK COMPLETED
2026-01-31 | 8:20 | 120260919 | 120260483 | 1 | AMC | AD COOP/DEYAAR | BIN AL JESSREEN | AUH | FAN MOTOR SOUND IN ROOF TOP | TROVEE | OLIVER | 9:10 | 9:32 | FOUND FAN MOTOR DAMAGE | NEED: CONDENSOR FAN MOTOR 3 UNIT NEED TO REPAIR |  | ATTENDED | NEED MATERIAL
2026-01-31 | 8:20 | 120260920 | 120260484 | 1 | AMC | NESTO | MALEHA | SHJ | FROZON CABINET | [7 empty] | ATTENDED | ATTENTED ON 2/2/2026
2026-01-31 | 15:00 | 120260921 | 120260485 | 2 | AMC | NESTO | AL MINA | DXB | FREEZERS TEMP.ISSUE | RACEL/MOHAMMED/SARAVANAN | GOVIND | 17:00 | 5:00 | FOUND LEAK IN 4 EVAPORATORE | USED:- 10 404A GAS |  | COMPLETED | WORK COMPLETED
2026-01-31 | 14:44 | 120260922 | 120260486 | 1 | AMC | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | EVAPORATORE FAN SOUND | RACEL |  | 20:13 | 21:05 | FOUND FAN BLADE AND HOLDER DAMAGE | NEED: FAN MOTOR AND FAN BLADE |  | ATTENDED | NEED MATERIAL
2026-01-31 | 3:31 | 120260923 | 120260487 | 1 | AMC | GRANDIOSE | MASDAR CITY | AUH | CHEESE CHILLER TEMP.ISSUE | RANDOLPH | TROVEE | 16:45 | 18:03 | FOUND THE COMPRESSOR MACHANICAL FAILURE | NEED :COMPRESSOR AND INSTALATION MATIREALS |  | ATTENDED | NEED MATERIAL
2026-01-31 | 15:07 | 120260924 | 120260488 | 1 | AMC | GOURMET | 1004 | AUH | PPM
2026-01-31 | 16:18 | 120260925 | 120260489 | 1 | AMC | HOP | JEBAL ALI | DXB | COLD ROOM DOOR ICE FORMATION | SADAM | ZALAUDIN | [5 empty] | ATTENDED | ATTENTED 1/2/2026
2026-01-31 | 16:35 | 120260926 | 5000218671 | 2 | AMC | ENOC | 4016 | DXB | 2 ND CHILLER NOT WORKING | SARAVANAN | [6 empty] | ATTENDED | ATTENTED ON 2-2-2026
2026-01-31 | 115:19 | 120260927 | 120260490 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | DRINKS CHILLER NOT WORKING | RANDOLPH | TROVEE | 15:50 | 16:15 | FOUND SOCKET HAS NO POWER AND /USED EXTENTION NOW UNIT IS WORKING | NEED : NEED TO REPAIR SOCKET |  | COMPLETED | WORK COMPLETED
2026-01-31 | 115:19 | 120260928 |  | 0 | AMC | ENOC | 1055 | DXB | WALKIN CHILLER HIGH TEMP | SADAM | ZALAUDIN | 21:45 | 1:35 | FOUND LEAK IN SECTION VALVE /AFTER REPAIR LEAK NOW UNIT IN NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-31 | 20:00 | 120260929 |  | 0 | AMC | ENOC | 1011 | DXB | OPEN CHILLER HIGH TEMP | SADAM | ZALAUDIN | 2:00 | 2:30 | OPEN CHILLER PAREMETER HIGH /AFTER ADJUST NOW SYSTEM RUNNING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-01-31 | 16:34 | 120260930 | PPM | 37 | AMC | ENOC | 1027 | DXB | Q 4 PPM | MUTHUKUMAR | SHAHABUDIN | [5 empty] | COMPLETED | WORK COMPLETED
2026-01-31 |  | 120260931 | 5000217631 | 2 | AMC | ENOC | 1142 | SHJ | FREEZER COLD ROOM WATER LEAK | AHSAN | SELVAN | 20:55 | 21:35 | FOUND DRAIN HEATER AND DRAIN PIPE NEED TO BE CHANGE | NEED: DRAINHEATER AND DRAIN FITTINGS |  | ATTENDED | NEED MATERIAL
2026-01-31 | 20:00 | 120260932 | 120260261 | 2 | AMC | AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE POWER TRIPPING | RANDOLPH | TROVEE | 18:30 | 19:45 | FOUND GEAR MOTOR DEFECTIVE, NEED TO REPLACE | USED: GEAR MOTOR-1NO CONDENCER FAN MOTOR - BY BRANCH |  | COMPLETED | WORK COMPLETED
2026-01-31 |  | 120260933 | 120260493 | 1 | AMC | AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE POWER SWITCH | OLIVER | FROILAN | 19:00 | 21:40 | FOND ROCKER SWITCH AN FAN MOTOR NEED TO BE CHANGE | NEED: ROCKER SWITCH 20A DPDT - 1NOS, FAN MOTOR 35 W 220V- 1 NOS |  | ATTENDED | NEED MATERIAL
2026-01-31 | 22:39 | 120260934 | 120260502 | 2 | AMC | NESTO | AJE | AJM | DELI CHILLER TEMP ISSUE. | VIGNESH | SELVAN | [5 empty] | ATTENDED | ATTENDED ON 1/2/2026
2026-01-31 |  | 120260935 | DRIVING | 27 | AMC |  |  |  | DRIVING | WILSON | [6 empty] | COMPLETED | WORK COMPLETED
2026-02-01 | 14:46 | 220260001 | 220260494 | 1 | AMC | AD COOP/DEYAAR | SPAR EXPRESS OMEGA TOWER | AUH | CHILLER WATER LEAK | TROVEE | RANDOLPH | 15:20 | 16:00 | FOUND DRAIN PIPE NOT PROPERLY AFERT REPAIR NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-01 | 1:34 | 220260002 | 220260495 | 1 | AMC | LULU | DHAID | SHJ | BACK STORE FREEZER 1 COMPRESSOR NOT WORKING | VIGNESH | SELVAN | 7:30 | 9:00 | FOUND ISOLATER HAS OFF AFTER ON NOW SYSTEM IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-01 | 9:45 | 220260003 | 220260496 | 1 | AMC | LULU | NUAIMIA | AJM | CHEESE DELI CHILLER TEMP ISSUE. | VIGNESH | SELVAN | 9:50 | 11:00 | FOUND CONDENSOER BLOCK AFTER CLEAN CONDENSOER NOW UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-01 | 10:39 | 220260004 | 220260497 | 2 | AMC | ANSAR | KARAMA | DXB | WATER LEAK | [7 empty] | ATTENDED | ATTENTED ON 2/2/2026
2026-02-01 | 15:13 | 220260005 | 220260498 | 1 | AMC | CAREEM | CITY LAND | DXB | WATER LEAK IN DRAIN PUMP | MUTHUKUMAR | MUSTAFA | 17:15 | 15:50 | FOUND MOISTURE IN DRAIN PUMP WATER LEAK NEED TO INSULATED | NEED : INSULATION SHEET - 1 MTR |  | ATTENDED | NEED MATERIAL
2026-02-01 | 19:39 | 220260006 | 220260499 | 1 | AMC | BAQER MOHEBI | SATWA | DXB | BAKERY CHILLER TRIPPING | RACEL |  | 20:34 | 21:47 | TRIPING FROM SINGLE POLE IN ELECTRICAL ROOM | USED: SOCKET 15 AMP - 1NOS FROM BACK STORE |  | COMPLETED | WORK COMPLETED
2026-02-01 | 18:21 | 220260007 | 220260500 | 1 | AMC | HOP | JEBAL ALI | DXB | ELCB TRIPPING AND DRAIN TRAY FULL ICE | MUTHUKUMAR | MUSTAFA | 18:21 | 21:10 | CHECKED AND FOUND DRAIN HEATER DAMAGE | USED: DRAIN HEATER 2 METER - 1NOS, |  | COMPLETED | WORK COMPLETED
2026-02-01 | 23:15 | 220260008 | 220260501 | 1 | AMC | PASONS | FUJEIRAH | FUJ | FREEZER BACK STORE COLD ROOM FAN NOT WORKING | RACEL |  | 0:25 | 1:50 | NEED TO CHANGE FAN MOTOR S4E300-AS72-53-220 AXEL FAN | NEED:- S4E300-AS72-53-220 AXEL FAN - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-01 | 22:39 | 220260009 | 120260502 | 2 | AMC | NESTO | AJE | AJM | DELI CHILLER TEMP ISSUE. | VIGNESH | SELVAN | 11:35 | 13:00 | FOUND CONDRNSOER BLOCK AFTER CLEAN CONDENSER NOW SYSTEM WORKING NORMAL |  | RECOMMEND NEED TO DELI CHILLER LEAK TEST NO:3 | COMPLETED | WORK COMPLETED
2026-02-01 | 9:35 | 220260010 | 220260503 | 1 | AMC | NESTO | KARAMA | DXB | LIGHTS CHECK | MUTHUKUMAR | MUSTAFA | 13:40 | 16:25 | FOUND MSB TRIP FOR TUB LIGHTS AFTER TURN ON NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-01 | 19:41 | 220260011 | 220260504 | 1 | AMC | NESTO | AL AIN | AL AIN | END WALL BROKEN | TALIB | [6 empty] | ATTENDED | ATTENTED ON 2/2/2026
2026-02-01 | 16:35 | 220260012 | 5000218671 | 2 | AMC | ENOC | 4016 | DXB | 2 ND CHILLER NOT WORKING | SARAVANAN | SHABEEB | 21:10 | 21:25 | FOUND UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-01 | 21:29 | 220260013 | 5000218812 | 1 | AMC | ENOC | 1074 | DXB | VERTICAL FREEZER NOT WORKING | SARAVANAN | SHABEEB | 21:55 | 22:05 | FONUD POWER PLUG IS LOSE /AFTER CONNECT PROPER NOW UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 7:00 | 220260014 | 220260505 | 2 | AMC | AD COOP/DEYAAR | MEGAMALL MEGAMART | SHJ | BUTCHERY CHILLER HIGH TEMP. | VIGNESH |  | 8:30 | 10:00 | FOUND EVAPORATORE COL LEAK FOR BRAZING NEED PERMIT AS PER STORE |  |  | ATTENDED | RESCHEDULE
2026-02-02 | 7:00 | 220260015 | 220260506 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | CHILLER CONDENSER FAN MOTOR FAN TRIPPING | RANDOLPH | TROVEE/ALLAN | 11:20 | 12:40 | FOUND RACK CONDENSSER FAN SHORTED AND /CHANGED REPAIRED FAN MOTOR FROM BRANCH AND NEED TO CHANGE REPAIR FAN |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 7:00 | 220260016 | 220260507 | 1 | AMC | AD COOP/DEYAAR | AWQAF | SHJ | WATER LEAK AT CHEESE DISPLAY C-5 AND VEGETABLE CHILLER DISPLAY | FROILAN | OLIVER /WILLIOM | 17:10 | 17:41 | FOUND WATER LEAK DUE TO DRAIN BLOCK AFTER DRAIN BLOCK REMOVED NOW UNIT OK |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 8:11 | 220260017 | 220260508 | 1 | AMC | AD COOP/DEYAAR | MBZ | AUH | NO AIR FLOW IN BED FREEZER | OLIVER | FROILAN/WILLIOM | 9:20 | 10:45 | FOUND ICE FORMATION /AFTER REMOVE ICE SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 9:06 | 220260018 | 220260509 | 2 | AMC | AD COOP/DEYAAR | MUROOR | AUH | ICE FORMATION | OLIVER | FROILAN/WILLIOM | 11:14 | 12:20 | FOUND ICE FORMATION IN SUCTION LINE AND NOISE IN FAN MOTORS | NEED :- ELCO FAN MOTOR-16 25W-1 NOS, 34 45W-1NOS, RUBBER INSULATION 11/8 X 3/8 - 25 MTR, FOAM TAP - 1 NOS, INSULATION GLUE-1 NOS. |  | ATTENDED | NEED MATERIAL
2026-02-02 | 9:35 | 220260019 | 220260510 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | CHEESE CHILLER TEMP ISSUE. | [6 empty] | BEFORE TEAM REQUESTED TO REPLACEMENT EVAPORATOR | ATTENDED | NEED MATERIAL
2026-02-02 | 9:35 | 220260020 | 220260511 | 1 | AMC | AD COOP/DEYAAR | ABU DHABI | AUH | FROZEN SECTION WATER LEAKAGE | RANDOLPH | TROVEE/ALLAN | 18:45 | 19:00 | FOUND WATER BLOCKE IN DRAIN LINE NOW AFTER VACCUM NOW NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 8:27 | 220260021 | 220260512 | 1 | AMC | TCS | UMS | DXB | FISH DISPLAY CHILLER WATER LEAKAGE | SADAM | ZALAUDIN | 9:30 | 10:55 | FOUND DRAIN PIPE BLOCK AFTER CLEAN NOW OK |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 11:43 | 220260022 | 220260513 | 1 | AMC | CAREEM | MARINA | DXB | SOME DOOR STRIP LIGHT NOT WORKING | SARAVANAN | SHABEEB | 2:30 | 2:40 | CHECKED AND FOUND NEED TO BE REPLACE LIGHTS | NEED:- LED LAMP SET LG-JST_5234_6814 SIZE 1400MM-240V SLIM TYPE WHITE - 1NOS |  | ATTENDED | NEED MATERIAL
2026-02-02 | 12:19 | 220260023 | 220260023 | 2 | AMC | AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE NOT WORKING | OLIVER | FROILAN/WILLIOM | 16:20 | 16:45 | FOUND THE UNIT CONDENSER NOT WORKING | NEED:- 35-45W - - 1NOS FAN MOTOR |  | ATTENDED | ATTENTED 3/2/2026
2026-02-02 | 10:21 | 220260024 | 220260024 | 1 | AMC | TCS | ROVE HEALTH CARE | DXB | WATER LEAK | MOHAMMED |  | 13:00 | 14:30 | FOUND BLOCK DRAIN /AFTER REMOVE BLOCK NOW NO WATER LEAKAGE |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 12:21 | 220260025 | 220260025 | 1 | AMC | BANIYAS COOP | SARAB | AUH | BAKERY CHILLER NOT WORKING | RANDOLPH | TROVEE/ALLAN | 15:25 | 16:00 | AFTER ICE MELTING FROM EVAPORATOR COIL NOW TEMP. IS NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260026 | 220260026 | 1 | AMC | PASONS | FUJEIRAH | FUJ | COLD ROOM HIGH TEMP | SABITH ALI |  | 11:15 | 13:30 | FOUND OUT SOLINOID COIL DEFFECTIVE | USED:- SOLINOID COIL DANFOSS - 1 NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260027 | 220260027 | 1 | AMC | BAQER MOHEBI | ABU HAIL | SHJ | COMBI FREEZER NO COOLING | VIGNESH |  | 15:35 | 19:00 | FOUND FULL OFF ICE FORMATION /AFTER REMOVE ICE NOW UNIT IS NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 17:00 | 220260028 | 120260485 | 2 | AMC | NESTO | AL MINA | DXB | FREEZERS TEMP.ISSUE | RACEL/MOHAMMED/SARAVANAN | GOVIND | 17:00 | 5:00 | FOUND LEAK IN 4 EVAPORATORE | NEED :- 20 404 A MORE FOR STABLE SYSTEM (NOW TEMP.IS NORMAL) |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260029 | 220260029 | 2 | AMC | BAQER MOHEBI | WAREHOUSE | DXB | CHILLER NOT WORKING | [7 empty] | NOT ATTENDED | 3/2/2026 SCHEDULED
2026-02-02 |  | 220260030 | 220260030 | 1 | AMC | LULU | AL AIN | AL AIN | DISPLAY CHILLER ARE NOT WORKING | TALIB | DENNIS | 17:30 | 23:00 | FOUND CHILLER SYSTEM SHUT DOWN AFTER WE RESET OVER LOADER AND ALARM SYSTEM NOW SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260031 | 220260031 | 2 | AMC | BAQER MOHEBI | SATWA | DXB | NEED TO CHANGE LIGHT WITH FRAME IN BAKERY SECTION | [7 empty] | NOT ATTENDED | 3/2/2026 SCHEDULED
2026-02-02 | 16:00 | 220260032 | 220260032 | 2 | AMC | AD COOP/DEYAAR | HAMDAN | AUH | WATER LEAKAGE | RANDOLPH | TROVEE/ALLAN | 19:27 | 20:02 | FOUND DRAIN PAN WAS DAMAGE | NEED:- DRAIN PAN |  | ATTENDED | NEED MATERIAL
2026-02-02 | 14:00 | 220260033 | 220260033 | 1 | AMC | AD COOP/DEYAAR | BIN AL JESSREEN | AUH | CHILLER NOT WORKING | OLIVER | FROILAN/WILLIOM | 1:15 | 3:24 | DUE TO ICE FORMATION THERE IS NO AIR FLOW /AFTER CLEAN ICE FORMATION NOW UNIT IS UNDER OBSERVATION |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 14:00 | 220260034 | 220260034 | 2 | AMC | AD COOP/DEYAAR | BIN AL JESSREEN | AUH | TABLE TOP CHILLER HIGH TEMP.ISSUE | OLIVER |  | 13:15 | 13:50 | FOUND COMPRESSER DAMAGE | NEED:- COMPRESSER AND GAS |  | ATTENDED | NEED MATERIAL
2026-02-02 |  | 220260035 | 7100294281 | 2 | AMC | ENOC | 1033 | DXB | WALK IN FREEZER ICE FORMATION | SARAVANAN | SHABEEB | 0:45 | 1:00 | PVC CURTAIN DAMAGE REPLACED |  |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260036 | 7100293384 | 2 | AMC | ENOC | 1017 | DXB | ABOVE THE OPEN CHILLER CABINET SHELF BOT | SARAVANAN | SHABEEB | 2:00 | 2:10 | CABINET TOP AREA IS OPEN NEED TO CLOSE AREA IT IS NOT OUR SCOOP |  |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260037 | 7100294778 | 1 | AMC | ENOC | 1080 | DXB | WATER LEAKAGE IN CHILLER | SADAM | ZALAUDIN | 11:30 | 12:00 | DRAIN PIPE LINE UNDER CONSEILD IN LEAKAGE /NOT IN OUR SCOPE |  |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260038 | 7100294805 | 1 | AMC | ENOC | 1025 | DXB | WALK IN CHILLER DOOR NOT CLOSING | SADAM | ZALAUDIN | 12:45 | 1:05 | FOUND DOOR HINGES AND DOOR GASKET DAMAGE | NEED:- DOOR HINGES - 1 SET, DOOR GASKIT-1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-02 |  | 220260039 | 7100294904 | 1 | AMC | ENOC | 1077 | DXB | WALK IN FREEZER WATER LEAK | SADAM | ZALAUDIN | 1:45 | 2:30 | WATER LEAK FROM BOADY SCREW APPLIED SILICON NOW NO LEAKAGE |  |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260040 |  | 0 | AMC | ENOC | 1501 | DXB | DISPLAY CHILLER UNITS WATER LEAKAGE ISSUE | SABITH ALI |  | 14:20 | 14:45 | DRAIN PAN AND DRAIN HEATER NEED TO BE CHANGE NOW UNIT IS NORMAL | NEED:- DRAIN PAN AND DRAIN HEATER |  | ATTENDED | NEED MATERIAL
2026-02-02 |  | 220260041 | 7100294861 | 2 | AMC | ENOC | 1634 | DXB | WALK IN CHILLER ICE FORMATION | SADAM | ZALAUDIN | 14:45 | 16:05 | FOUND ICE FORMATION IN EVAPORATER SFTER CLEAN EVAPORATOR NOW UNIT IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 3:58 | 220260042 | 220260042 | 1 | AMC | COLOURS EXPRESS | SUPER MARKET | AUH | CHILLER NOT WORKING | RANDOLPH | TROVEE/ALLAN | 17:10 | 17:50 | FOUND CONDENSSER FAN MOTOR AND VEG SECTION CONTACTOR DEFFECTIVE | NEED:- CONTACTORS AND 3 PHASE CONDENSSER FAN MOTOR |  | ATTENDED | NEED MATERIAL
2026-02-02 | 12:21 | 220260043 | 220260043 | 1 | AMC | BANIYAS COOP | SHAHAMA | AUH | FREEZER NOT WORKING | RANDOLPH | TROVEE/ALLAN | 14:24 | 14:50 | FOND OUT THE COMPRESSOER DEFFECTIVE NEED TO BE REPLACE | NEED:- COMPRESSOER AND INSTALATION MATIREALS |  | ATTENDED | NEED MATERIAL
2026-02-02 | 9:00 | 220260044 | 220260497 | 2 | AMC | ANSAR | KARAMA | DXB | WATER LEAK | MOHAMMED |  | 10:00 | 12:08 | FOUND THE DISPLAY CHIULLER DAMAGE CHANGED THE CONTROLLER /DELI CHILLER NEED TO REPROSSES SYSTEM | USED :- DISPLAY CONTROLER/ NEED:- REPROSSES MATIREALS |  | ATTENDED | NEED MATERIAL
2026-02-02 |  | 220260045 | 220260045 | 1 | AMC | NESTO | MALEHA | SHJ | BUTCHERY CHILLER HIGH TEMP. | VIGNESH |  | 23:00 | 1:30 | FOUND CONTROLER ISSUE AFTER REPAIR WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260046 | 220260046 | 1 | AMC | ADNOC | 227 | DXB | ICE MACHINE COMPLENT | MOHAMMED |  | 16:00 | 21:20 | FOUND OUT SOLENOID COIL VALVE DAMAGE /AFTER CHANGING WORKING NORMAL | USED:- SOLENOID COIL - 1 NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260047 | 220260047 | 1 | AMC | ADNOC | 173 | AUH | BAKERY CHILLER CLEAN | [7 empty] | NOT ATTENDED | OUT OF WARRENTY
2026-02-02 | 10:30 | 220260048 | 7100294882 | 1 | AMC | ENOC | 1011 | DXB | CALIBRATION REQUEST FOR CHILLER/FREEZER | [7 empty] | NOT ATTENDED | NOT OUR SCOPE
2026-02-02 | 10:30 | 220260049 | 7100294885 | 1 | AMC | ENOC | 1029 | DXB | Store refrigeration required PM | [7 empty] | NOT ATTENDED | SCHEDULED
2026-02-02 | 10:30 | 220260050 | 7100294893 | 2 | AMC | ENOC | 1056 | DXB | vertical freezer 1 light busted | [7 empty] | ATTENDED | ATTAINED ON 04/2/2026
2026-02-02 | 10:30 | 220260051 | 7100294894 | 1 | AMC | ENOC | 1057 | DXB | Chiller Door 1 to 10 1 no. light is bust | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-02 | 10:30 | 220260052 | 7100294809 | 2 | AMC | ENOC | 1027 | DXB | ICE IS BUILDING UP ON DISPLAY PRODUCTS I | SARAVANAN | SHABEEB | 3:20 | 3:30 | FOUND DOORS GASKIT DAMAGE NEED TOBE REPLACE | NEED :- GASKIT |  | ATTENDED | NEED MATERIAL
2026-02-02 | 10:30 | 220260053 | 7100294815 | 2 | AMC | ENOC | 1041 | DXB | walk in chiller door rubber damaged need | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-02 | 10:30 | 220260054 | 7100294817 | 2 | AMC | ENOC | 1041 | DXB | chiller shelf rusty need to change | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-02 | 10:30 | 220260055 | 7100294820 | 1 | AMC | ENOC | 1055 | DXB | Walk in chiller temperature fluctuating | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-02 | 10:30 | 220260056 | 7100294827 | 2 | AMC | ENOC | 1205 | DXB | lights (walk in chiller) | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-02 |  | 220260057 | 220260057 | 1 | AMC | ENOC | 1058 | DXB | PPM | MUTHUKUMAR | SHAHABUDIN |  |  | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-02 |  | 220260058 | 220260058 | 1 | AMC | ENOC | 1063 | DXB | PPM | MUTHUKUMAR | SHAHABUDIN |  |  | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 19:00 | 220260059 | 7100294809 | 2 | AMC | ENOC | 1103 | SHJ | WALK IN CHILLER GASKIT DAMAGE | AHSAN | SELVAN | 22:40 | 23:00 | FOUND 7 DOORS GASKIT DAMAGED | NEED:- 7 DOORS GASKIT |  | ATTENDED | NEED MATERIAL
2026-02-02 | 15:09 | 220260060 | 220260060 | 3 | AMC | NESTO | AJE | AJM | HOT CABIN ISSUE. | AHSAN | SELVAN | 20:35 | 21:45 | FOUND BIRIYANI COUNTER AND FOOD COUNTER NO.3 NEED TO BE CHANGE HEATER | NEED:- HEATER 5 AMS - 1 NIOS,12APMS CONDACTOR - 1NOS, HEATER 5 AMS - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-02 | 15:09 | 220260061 | 220260060 | 3 | AMC | NESTO | AJE | AJM | NEED TO INSPECT ALL UNIT HOT FOOD | AHSAN | SELVAN | 2:50 | 4:00 | AS PER STORE VISIT ALL UNITS ARE DAMAGE AND CONTROLLERS BOX ALLSO DAMAGE COIL ALSO NOT PROPER AIR SARCULATION |  | BETTER TO CHANGE THE UNITS | COMPLETED | WORK COMPLETED
2026-02-02 | 20:00 | 220260062 | 220260062 | 1 | AMC | BLUE WATER MARINA | BANIYA FOREST | DXB | PPM | SARAVANAN | SHABEEB | [5 empty] | COMPLETED | WORK COMPLETED
2026-02-02 | 20:00 | 220260063 | 220260063 | 1 | AMC | NESTO | AJE | AJM | PPM | ABHIJITH | SUDHEESH | [5 empty] | COMPLETED | WORK COMPLETED
2026-02-02 | 9:00 | 220260064 | 220260505 | 2 | AMC | AD COOP/DEYAAR | MEGAMALL MEGAMART | SHJ | BUTCHERY CHILLER HIGH TEMP. | AHSAN | SELVAN |  | 2:12 | FOUND EVAPORATORE COL LEAK FOR BRAZING NEED PERMIT AS PER STORE/DONE WITH BRAZING |  |  | COMPLETED | WORK COMPLETED
2026-02-02 | 8:00 | 220260065 | 220260065 | 1 | AMC | ENOC | 1005 | DXB | PPM | BIJU | TALHA | [5 empty] | COMPLETED | WORK COMPLETED
2026-02-02 | 7:00 | 220260066 | 220260066 | 1 | AMC | TD | DRIVING | DXB | DRIVING | WILSON |  | 9:00 | 19:45 |  |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 8:00 | 220260067 | 220260029 | 2 | AMC | BAQER MOHEBI | WAREHOUSE | DXB | CHILLER NOT WORKING | SADAM | ZALAUDIN | 9:00 | 10:20 | CHECKED SYSTEM RUNNING NORMAL SYSTEM UNDER OBSERVETION |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 8:00 | 220260068 | 220260031 | 2 | AMC | BAQER MOHEBI | SATWA | DXB | NEED TO CHANGE LIGHT WITH FRAME IN BAKERY SECTION | AHSAN | SELVAN | 0:10 | 2:00 | FOUND THE BAKERY CHILLER NEED THE LIGHT | NEED: 4 FEET LIGHT WARM WHITE |  | ATTENDED | NEED MATERIAL
2026-02-03 | 7:57 | 220260069 | 220260069 | 1 | AMC | WESTLAND | AL AIN | AL AIN | OUT DOOR ICE FORMATION | TALIB |  | 3:30 | 5:50 | FOUND ICE FORMATION EVAPORATOR AFTER REMOVE ICE NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 8:25 | 220260070 |  | 0 | AMC | ENOC | 1060 | DXB | BED FREEZER NOT WORKING | SADAM | ZALAUDIN | 18:45 | 20:00 | REPLACE BOX FAN NOW WORKING NORMAL | USED: FAX 120 X 120 - 1NOS |  | ATTENDED | ATTAINED ON 03/2/2026
2026-02-03 | 8:25 | 220260071 | 220260071 | 1 | AMC | NESTO | MUSAFFAH | AUH | ICE MACHINE NOT WORKING | RANDOLPH | TROVEE | 20:00 | 20:45 | RESET THE UNIT AND RECHARGE THE GAS | USED: R 404A - BY TD |  | COMPLETED | WORK COMPLETED
2026-02-03 | 9:07 | 220260072 | 220260072 | 1 | AMC | NESTO | AJE | AJM | CHILLERS TEMP ISSUE. | RACEL |  | 9:39 | 13:30 | FOUND SENSOR IS NOT WORKING PROPERLY AFTER CHANGING SENSOR NOW CHILLER NORMAL TEMP. | USED:- NTC SENSOR - 2NOS |  | COMPLETED | WORK COMPLETED
2026-02-03 | 9:20 | 220260073 | 220260073 | 1 | AMC | NESTO | AJE | AJM | BACK STORE CHILLER TEMP. ISSUE | RACEL |  | 10:00 | 13:31 | AKO CONTROLLER AND SENSOR NEED TO BE CHANGE | NEED:- CONTROLLER -1NOS,SENSOR-2NOS |  | ATTENDED | NEED MATERIAL
2026-02-03 | 9:36 | 220260074 | 220260074 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | CHILLER NOT COOLING | RANDOLPH | TROVEE | 8:20 | 10:31 | FOUND THE WATER FLOW FROM FLOOR DRAIN /AFTER CLEAN NOW UNIT NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 9:38 | 220260075 | 220260075 | 1 | AMC | AD COOP/DEYAAR | ZAKHER MALL | AUH | DISPLAY FREEZER NOT COLLING | TALIB |  | 9:50 | 14:05 | AFTER WATER SERVICE AND CHANGE FAN MOTOR 10 W NOW SYSTEM IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 8:17 | 220260076 | 220260076 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | F 11 FREEZER WATER LEAKAGE | RANDOLPH | TROVEE/OLIVER | 11:18 | 11:35 | FOUND WATER LEAK DUE TO MOISTURE OF CABINET NEED TO INSTALL FAN FOR SOLUTION | NEED:- AXIAL FAN 120 X 120 -N 10 NOS, CABLE TIE - 1 PKT |  | ATTENDED | NEED MATERIAL
2026-02-03 | 9:02 | 220260077 | 220260077 | 1 | AMC | AD COOP/DEYAAR | ABU DHABI | AUH | CHILLER C9 WATER LEKAGE | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-03 | 9:43 | 220260078 | 7100294861 | 2 | AMC | ENOC | 1634 | DXB | WALK IN CHILLER ICE FORMATION | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-03 | 11:05 | 220260079 | 220260079 | 4 | AMC | GRANDIOSE | SOUQ AL BAHAR | DXB | NEED TO CHECK COMPRESSOR |  |  |  |  | NEED TO TAKE PASS |  |  | ATTENDED | ATTEND ON 9/2/2026
2026-02-03 | 12:05 | 220260080 | 7100295086 | 1 | AMC | ENOC | 4002 | DXB | WATER LEAKAGE FROM CHILLER 2 | SABITH ALI |  | 16:25 | 17:10 | REMOVED THE DRAIN BLOCK NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 12:05 | 220260081 | 7100295161 | 1 | AMC | ENOC | 1511 | SHJ | PRONTO VERTICAL FREEZER IS NOT WORKING | RACEL |  | 18:33 | 10:20 | FOUND OUT NO POWER SUPPLY DEFFECT OF COMPRESSER | NEED:- SC21CL SECOP COMPRESSOR AND INSTALATION SPARE |  | ATTENDED | NEED MATERIAL
2026-02-03 | 12:05 | 220260082 | 7100295232 | 1 | AMC | ENOC | 4037 |  | CHILLER TEMP.GAUGE | SARAVANAN | SHABEEB | 20:15 | 21:20 | FOUND LESS GASS AFTER TOPUP NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 12:05 | 220260083 | 7100295233 | 1 | AMC | ENOC | 1060 |  | BED FREEZER NOT WORKING | SADAM | ZALAUDIN | 18:45 | 20:00 | REPLACE BOX FAN NOW WORKING NORMAL | USED: FAX 120 X 120 - 1NOS |  | COMPLETED | WORK COMPLETED
2026-02-03 | 11:39 | 220260084 | 220260023 | 2 | AMC | AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE NOT WORKING | RANDOLPH | TROVEE/OLIVER | 11:50 | 12:30 | FAN MOTOR CHANGED |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 12:56 | 220260085 | 220260085 | 2 | AMC | NESTO | WAREHOUSE | DXB | WATER LEAKAGE | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-03 |  | 220260086 | 7100293769 | 2 | AMC | ENOC | 1444 | RAK | DOOR FRAME FALL DOWN | SABITH ALI |  | 13:10 | 13:50 | FOUND HANDELS SCREW ARE DAMAGE CHANGED THE SCREW AND FIXED THE HANDEL NOW SYSTEM IS NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 15:07 | 220260087 | 220260087 | 2 | AMC | AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | FREEZER TEMP ISSUE. | TROVEE | RANDOLPH/OLIVER | 15:40 | 16:00 | FOUND OUT SOLAR DISPLAY AND IN BUTCHERY SECTION DIXELL CONTROLLER DEFECT NEED TO CHANGE | NEED: CONTROLLER DIXELL-1 NOS , SOLAR DISPLAY , CONTACTOR LC125 |  | ATTENDED | NEED MATERIAL
2026-02-03 | 15:07 | 220260088 | 220260088 | 2 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | ICE MACHINE NOT WORKING | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-03 | 15:07 | 220260089 | 220260087 | 2 | AMC | AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | BUTCHERY CHILLER NOT WORKING | TROVEE | RANDOLPH/OLIVER | 15:40 | 16:00 | FOUND OUT SOLAR DISPLAY AND IN BUTCHERY SECTION DIXELL CONTROLLER DEFECT NEED TO CHANGE | NEED: CONTROLLER DIXELL-1 NOS , SOLAR DISPLAY , CONTACTOR LC125 |  | ATTENDED | NEED MATERIAL
2026-02-03 | 15:35 | 220260090 | 220260090 | 1 | AMC | AD COOP/DEYAAR | MUROOR | AUH | BUTCHERY WALK IN CHILLER TRIPPED 3 TIMES | RANDOLPH | TROVEE/OLIVER | 16:27 | 17:00 | FOUND THE DEFROST HETER SHORT AFTER RECTIFY NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 12:00 | 220260091 | 220260091 | 1 | WTY | ADNOC | 639 | AUH | HOT GRILLER NOT WORKING | ALLAN | WILLIAM | 13:30 | 14:50 | ADJUST THE ALLENED NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 16:49 | 220260092 | 220260092 | 2 | AMC | AD COOP/DEYAAR | BIN AL JESSREEN | AUH | MEET CHILLER TEMP.ISSUE | RANDOLPH | TROVEE/OLIVER | 17:20 | 18:30 | CHANGED THE REPAIRED CONDENSER FAN MOTOR BY DEYAAR | NEED:- DANFOSS SOLENOID VALVE 3/8, R404 |  | ATTENDED | NEED MATERIAL
2026-02-03 | 17:02 | 220260093 | 220260093 | 3 | AMC | ANSAR | KARAMA | DXB | FREEZER UNIT SHUT OFF | AHSAN | SELVAN | 19:50 | 22:00 | NOW RESET THE MOTOR PROTECTOR NOW WORKING NORMAL /BUT NEED MOTOR PROTECTOR | NEED:- MOTOR PROTECTOR |  | ATTENDED | NEED MATERIAL
2026-02-03 | 16:00 | 220260094 | 7100293944 | 3 | AMC | ENOC | 509 | FUJ | LIGHT CHANGE | RACEL |  | 16:23 | 16:58 | CHANGED LIGHTS |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 9:00 | 220260095 | 120260445 | 2 | AMC | GRANDIOSE | WASL VILLAGE | DXB | PORK SECTION TEMP ISSUE | VIGNESH | SADAM | 11:40 | 17:20 | STUCK-UP MECHANICAL OF COMPRESSOR | USED:- NJX2219GK -1 NOS, FILTER DRIER 3/8-1 NOS,R404-1CYLD,NITROGEN-1CYLD,141B-1CYLD,BLUE ROD-4NOS,BRAZING ROD-8NOS,ORIFACE NO 1 - 1NOS. |  | COMPLETED | WORK COMPLETED
2026-02-03 | 18:12 | 220260096 | 220260096 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | FREEZER B35 NOT WORKING | OLIVER |  | 18:50 | 21:30 | DEFROST HEATER NEED TO BE CHANGE UNIT IS NOW UNDER OBSERVATION |  |  | ATTENDED | NEED MATERIAL
2026-02-03 | 20:00 | 220260097 | 220260097 | 1 | AMC | 77 TEXAS BBQ | SILICON OASSIS | DXB | PPM | SARAVANAN | SHABEEB |  |  | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 9:00 | 220260098 | 220260098 | 1 | AMC | NESTO | AJE | DXB | PPM | ABHIJITH | SUDHEESH |  |  | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-03 | 8:00 | 220260099 | 220260099 | 1 | AMC |  |  | DXB | DRIVING | WILSON |  | 8:45 | 22:20 | DUBAI -FLOWER SHOPE |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 20:00 | 220260100 |  | 0 | AMC | ENOC | 1080 | DXB | VERTICALE FREEZER ISSUE | SARVANAN | SHABEEB | 3:00 | 3:15 | FOUND FREEZER IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 0:00 | 220260101 | 220260101 | 1 | AMC | BAQER MOHEBI | SATWA | DXB | ICE CREAMFREEZER HIGH TEMP. | AHSAN | SELVAN | 22:30 | 2:00 | FOUND LOW GAS /AFTER GAS CHARGE NOW WORKING NORMAL | USED: 404 A - 1 NOS BY TD |  | COMPLETED | WORK COMPLETED | ATTEND ON 3/2/2026
2026-02-04 | 8:56 | 220260102 | 220260102 | 1 | AMC | EVERMORE | DIP | DXB | PPM | MUTHUKUMAR | SHAHABUDIN |  |  | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-04 |  | 220260103 | 220260103 | 1 | AMC | FLOWE SHOP | DUBAI | DXB | MONOBLOCK INSTALATION | DENNIS/MOHAMMED | ROJER |  |  | WORK DONE NEED TO BE OBSERTATION AFTER PANNEL WORK |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 9:07 | 220260104 | 220260104 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | MILK CHILLER COOLING ISSUE. | VIGNESH |  | 11:00 | 13:30 | FOUND OUT THE LESS GAS AFTER TOP UP AND CONDENSOR CLEAN NOW SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 9:14 | 220260105 | 220260105 | 1 | AMC | CAREEM | DFC | DXB | EGG CHILLER DOOR ISSUE. | SADAM | ZALAUDIN | 16:20 | 15:00 | FOUND THE DOOR SPRING AND GASKET DMAGE /WE REPAIRD NOW BUT NEED TO BE CHANGE | NEED:- DOOR SPRING-1NOS,DOOR GASKET-1NOS |  | ATTENDED | NEED MATERIAL
2026-02-04 | 11:00 | 220260106 | 220260106 | 1 | AMC | ANSAR | KARAMA | DXB | WATER LEAKAGE FROM DELI CHILLER AND VEGETABLE DISPLAY | VIGNESH |  | 13:55 | 15:00 | MAIN DRAIN LINE BLOCK /AFTER CLEAR DRAIN LINE NOW UNIT NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 9:00 | 220260107 | 220260107 | 1 | AMC | NESTO | AJE | DXB | CAKE DISPLAY TEMP. ISSUE | RACEL |  | 14:50 | 15:50 | FOUND ALL TEMP IS NORMAL AND CHECK AIRFLOW ALSO NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 11:38 | 220260108 |  | 0 | AMC | ENOC | 1634 | DXB | TEMP ISSUE. WALK IN CHILLER | MOHAMMED |  | 11:20 | 13:15 | REMOVE THE ICE FORMATION AFTER RESET THE DEFROST SETTINGS /NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 12:04 | 220260109 | 220260109 | 1 | AMC | NESTO | NADD AL HAMMAR | DXB | FZ 01 NOT WORKING | MOHAMMED |  | 14:40 | 16:25 | FOUND POWER CONTROLER SWITCH DAMAGE AFTER REPLACE WPRKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 12:18 | 220260110 | 220260110 | 1 | AMC | SWEET CONNECTION | DIP | DXB | FREEZER NOISE ISSUE | SADAM | ZALAUDIN | 14:10 | 15:08 | DOOE HEATER POWER CABLE REPAIRD NOW WORKING NOTMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 7:00 | 220260111 | 220260111 | 1 | AMC | LULU | DHAID | SHJ | COLD ROOM FREEZER HIGH TEMP. | RACEL |  | 8:00 | 12:45 | FOUND DRFECTIVE EVAPORATOR SENSOR /FOUND EVAPORATOR FAN MOTOR SLOW ROTATION. | USED:-NTC SENSOR -1 NOS/, NEED:-EVAPORATOR FAN MOTOR 75/85W - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-04 | 1:13 | 220260112 | 220260112 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | FISH STORE ROOM IS HIGH TEMP. | TROVEE | OLIVER | 14:48 | 15:20 | FOUND GAS LESS AFTER RECHARGE SYSTEM NOW WORKING NORMAL | NEED:- TUBE LIGHT ,CONDENSORE FAN MOTOR, |  | ATTENDED | NEED MATERIAL
2026-02-04 | 9:00 | 220260113 | 220260088 | 2 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | ICE MACHINE NOT WORKING | RANDOLPH | TROVEE | 11:10 | 11:47 | FOUND DELIVERD ICE MACHIAN WAS DAMAGE |  |  | COMPLETED | WORK COMPLETED
2026-02-04 |  | 220260114 |  | 0 | AMC | ENOC | 1064 | DXB | VERTICAL CHILLER RUBBER GASKET | MUSTAFA |  | 12:20 | 12:55 | NEED TO CHANGE GASKET | NEED:- GASKET -67 X 156.5 CM |  | ATTENDED | NEED MATERIAL
2026-02-04 | 8:00 | 220260115 | 220260085 | 2 | AMC | NESTO | WAREHOUSE | DXB | WATER LEAKAGE | SADAM | ZALAUDIN | 9:30 | 12:40 | FOUND EVAPORATOR AND FILTER BLOCK /AFTER CLEARE BLOCK NOW SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 14:03 | 220260116 | 220260116 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | BAKERY CHILLER TEMP ISSUE | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-04 | 14:38 | 220260117 | 220260117 | 1 | AMC | AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | FREZEER TEMP OK BUT ITEMS MELTING | VIGNESH |  | 15:56 | 18:00 | FOUND EVAPORATORE ICE FORMATION AFTER REMOVE ICE WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 10:00 | 220260118 | 220260118 | 1 | AMC | AD COOP/DEYAAR | ZAKHER MALL | AL AIN | FREEZER TEMP.ISSUE | TALIB |  | 10:15 | 13:45 | FOUND ICE FORMATION IN EAPORATOR/AFTER CLEAN NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 15:46 | 220260119 | 220260119 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | YOGURTS CHILLER DRIPPING | RANDOLPH | ALLAN | 16:40 | 17:54 | FOUND THE CONDENSOR FAN MOTOR 3 PHASE 23 X 27 /HAND OVER TO DEYAEER |  |  | ATTENDED | NEED MATERIAL
2026-02-04 | 15:46 | 220260120 | 120260372 | 3 | AMC | AD COOP/DEYAAR | AWQAF | AUH | REPLACE COMPRESSOR | TROVEE | OLIVER | 15:20 | 18:45 | REPLACED NEW COMPRESSOR PROVIDED BY STORE |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 17:43 | 220260121 | 220260121 | 1 | AMC | WAHAT AL MASA | RICE WAREHOUSE | AUH | 10 UNITS NEED TO CHECK TEMP. | RANDOLPH/TROVEE | OLIVER/ALLAN | 20:20 | 10:35 | NEED TO CHARGE GAS AND FILL COMPRESSOR OIL | NEED: COMPRESSOR OIL AND REFEIGERANT |  | ATTENDED | NEED MATERIAL
2026-02-04 |  | 220260122 | 7100294815 | 2 | AMC | ENOC | 1041 | DXB | walk in chiller door rubber damaged need | MOHAMMED |  | 17:20 | 18:38 | FOUND GASKET DAMAGE NEED TO REPLACE | NEED:- REPLACE GASKET |  | ATTENDED | NEED MATERIAL
2026-02-04 |  | 220260123 | 7100294817 | 2 | AMC | ENOC | 1041 | DXB | chiller shelf rusty need to change | MOHAMMED |  | 17:20 | 18:38 | FOUND ALL CHILLER SHELF ARE RUST NEED TO BE PAINTING | NEED:- NEED TOBE PAINTING |  | ATTENDED | NEED MATERIAL
2026-02-04 |  | 220260124 | 7100294893 | 2 | AMC | ENOC | 1056 | DXB | vertical freezer 1 light busted | SHABEEB |  | 21:25 | 21:52 | CHECKED THE FREEZER NEED TO CHANGE LIGHT SET | NEED :- FULL LIGHT SET 6500K |  | ATTENDED | NEED MATERIAL
2026-02-04 |  | 220260125 | 5000219334 | 1 | AMC | ENOC | 1060 | DXB | BED FREEZER NOT WORKING | SHABEEB |  | 1:15 | 1:51 | FOUND THERE IS A LEAK IN SECTION PIPE NEED TO RIX LEAKAGE /STORE NOT ALLOWED FOR DO THAT TIME . | NEED TO FIX LEAKAGE |  | ATTENDED | RESCHEDULE
2026-02-04 | 19:52 | 220260126 | 220260126 | 1 | AMC | HOP | JEBAL ALI | DXB | COLD ROOM TEMP. ISSUE | [7 empty] | ATTENDED | ATTAIND ON 5/2/2026
2026-02-04 | 20:13 | 220260127 | 220260127 | 1 | AMC | BAQER MOHEBI | AL NAHDA | DXB | BUTCHERY TABLE TOP CHILLER NOT WORKING | AHSAN |  | 21:00 | 22:10 | FOUND DEFROST BUTTON JAMM /AFTER CLEANING KET PAID NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 20:59 | 220260128 | 220260128 | 3 | AMC | BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER NO COOLING | AHSAN |  | 22:30 | 0:00 | NOW CHANGED THE WIRE UNIT IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 21:06 | 220260129 | 220260129 | 1 | AMC | BAQER MOHEBI | SATWA | DXB | BAKERY CHILLER NOT WORKING | SHABEEB |  | 23:00 | 0:10 | FOUND CONDENSOR BLOCK /AFTER CLEAN UNIT NOW WORKING |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 20:12 | 220260130 | 220260130 | 1 | AMC | NESTO | AJF | AJM | DELI CHILLER HIGH TEMP. | AHSAN |  | 1:35 | 3:00 | FOUND THE LESS GAS LEAK AFTER GAS CHARGE SYSTEM NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 21:00 | 220260131 | 220260131 | 1 | AMC | NESTO | AJC | AJM | PPM | ABHIJITH | SUDHEESH |  |  | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-04 | 8:00 | 220260132 | 220260132 | 1 | AMC |  | DRIVING | DXB | DRIVING | WILSON |  | 9:00 | 18:30 | DXB,AUH |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 7:00 | 220260133 | 220260133 | 1 | AMC | AMAZON | DXB 3 | DXB | Q 1 PPM | ABID | AJMEER/GOVIND | [5 empty] | COMPLETED | WORK COMPLETED
2026-02-05 | 8:10 | 220260134 | 220260134 | 1 | AMC | TCS | ROVE CITY CENTER | DXB | WATER LEAK IN CHILLER | SADAM | ZALAUDIN | 12:00 | 12:45 | CLEAND THE DRAIN PAN WITH VACCUM AND CHECKED THE DRAIN HEATER NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 8:10 | 220260135 | 220260135 | 1 | AMC | TCS | UMS | DXB | FREEZER TEMP. ISSUE | SADAM | ZALAUDIN | 9:30 | 11:00 | FREEZER NO 4,5,6 TEMP ISSUE /FOUND LESS GASS AFTER GAS CHARGE NOW WORKING NORMAL | USED: 404 A - 1 NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-02-05 | 9:00 | 220260136 | 220260032 | 2 | AMC | AD COOP/DEYAAR | HAMDAN | AUH | WATER LEAKAGE | OLIVER | RANDOLPH/TROVE | 8:33 | 9:15 | CHANGED DRAIN PAN WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 9:34 | 220260137 | 220260034 | 2 | AMC | AD COOP/DEYAAR | BIN AL JESSREEN | AUH | TWO UNDER COUNTER CHILLER AND FISHERY SECTION ARE NOT WORKING | [6 empty] | REQUESTED FOR SPARE PARTS | ATTENDED | NEED MATERIAL
2026-02-05 | 9:34 | 220260138 | 220260092 | 2 | AMC | AD COOP/DEYAAR | BIN AL JESSREEN | AUH | BUTCHERY CHILLER HIGH TEMP. | [6 empty] | REQUESTED FOR SPARE PARTS | ATTENDED | NEED MATERIAL
2026-02-05 | 11:49 | 220260139 | 220260112 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | NEED TO CHANGE LIGHT AND FAN MOTOR | RANDOLPH | TROVEE/OLIVER | 13:20 | 13:58 | CHANGEND THE FAN MOTOR | NEED:- DRAIN HEATER FOR PROMOTION CHILLER |  | ATTENDED | NEED MATERIAL
2026-02-05 | 9:01 | 220260140 | 220260140 | 1 | AMC | NESTO | AJG | AJM | DELI CHILLER BACK STORE LIGHT NOT WORKING | VIGNESH |  | 13:50 | 15:00 | CHENGED LIGHT | USED:- LIGHT 2 NOS |  | COMPLETED | WORK COMPLETED
2026-02-05 | 9:53 | 220260141 | 220260141 | 2 | AMC | NESTO | MALEHA | SHJ | SALAD COUNTER TEMP ISSUE. | [7 empty] | NOT ATTENDED | NOT OUR SCOPE
2026-02-05 | 11:00 | 220260142 | 7100295676 | 1 | AMC | ENOC | 1236 | AJM | door freezer light not working | VIGNESH |  | 15:10 | 15:50 | FOUND LED DRIVE COMPLENT NEED TO REPLACE | NEED :- LED DRIVE 240 - 24V -1NOS |  | ATTENDED | NEED MATERIAL
2026-02-05 | 7:05 | 220260143 |  | 0 | AMC | ENOC | 1505 | DXB | OPEN CHILLER HIGH TEMP | RACEL |  | 13:14 | 15:55 | LESS GAS FOUND LEAKAG AFTER ARREST LEAK NOW WORKING NORMAL | USED:- 404 A - 1NOS |  | COMPLETED | WORK COMPLETED
2026-02-05 | 12:02 | 220260144 | 7100293927 | 2 | AMC | ENOC | 1019 | DXB | LIGHT CHANGE | SABITH ALI |  | 13:10 | 14:00 | FOUND LIGHT DAMAGE AFTER CHANGE NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 3:24 | 220260145 | 220260145 | 1 | AMC | LULU | NUAIMIA | AJM | BAKERY CHILLER NOT WORKING | VIGNESH |  | 9:00 | 12:40 | FOUND BOX FAN NOT WORKING / AFTER CHANGED BOX FAN NOW WORKING NORMAL | USED:- 120 X 120 - 1 NOS BY BRANCH |  | COMPLETED | WORK COMPLETED
2026-02-05 | 10:58 | 220260146 | 220260146 | 1 | AMC | COLOURS EXPRESS | SUPER MARKET | AUH | DRINKS CHILLER NOT WORKING | RANDOLPH | TROVEE/OLIVER | 11:00 | 12:40 | FOUND OUT THE UNIT IS OFF /AFTER SYSTEM ON NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 12:29 | 220260147 |  | 0 | AMC | ENOC | 1401 |  | WALKIN FREEZER SHOUT DOWN | SABITH ALI |  | 10:30 | 12:15 | FOUND ICE FORMATION AFTER REMOVE ICE RESET UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED | ATTAIND ON 6/2/2026
2026-02-05 | 15:30 | 220260148 | 220260148 | 1 | AMC | AD COOP/DEYAAR | ZAYED 1ST | AUH | TUBE LIGHTS NOT WORKING IN FREEZER | RANDOLPH | TROVEE/OLIVER | 16:30 | 17:15 | FOUND OUT 7 NOS LIGHT BUSTED NEED TO REPLACE | NEED:- 7 NOS 2 FEET LIGHT ,DOUBLE SIDED TAPE-1 |  | COMPLETED | WORK COMPLETED
2026-02-05 | 13:46 | 220260149 | 220260149 | 1 | AMC | BANYA FOREST | BLUE WATER | DXB | AC NOT WORKING | SADAM | ZALAUDIN | 14:30 | 16:30 | FOUND AC RUNNING FAN MOTOR AFTER TURN ON COOLING MODE NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 13:59 | 220260150 | 220260150 | 1 | AMC | GOURMET | 1004 | AUH | FREEZER NOT WORKING | RANDOLPH | TROVEE/OLIVER | 20:00 | 20:30 | UNIT IS NOW SWITCH OFF NEE TO BE CHANGE FAM MOTOR AND GURD | NEED:- FAN MOTOR AND FAN GURD |  | ATTENDED | NEED MATERIAL
2026-02-05 | 13:59 | 220260151 | 220260128 | 3 | AMC | BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER NO COOLING | SABITH ALI |  | 15:40 | 17:30 | FOUND LESS GASS AFTER TOPUP NOW WORKING NORMAL | USED:- R22 GAS 2KG BY STORE |  | COMPLETED | WORK COMPLETED
2026-02-05 | 19:08 | 220260152 | 220260152 | 2 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | TABLE CHILLER HIGH TEMP.ISSUE | [7 empty] | ATTENDED | ATTAIND ON 6/2/2026
2026-02-05 | 16:00 | 220260153 |  | 0 | AMC | ENOC | 1057 | DXB | WALKIN CHILLER NOT WORKING | SADAM | ZALAUDIN | 17:00 | 18:00 | FOUND LOSE CONNECTION IN HOLDER AFTER REST NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 20:00 | 220260154 |  | 0 | AMC | CAREEM | CITY LAND | DXB | DRAIN PUMP WATER LEAKGE | SARAVANAN | SHABEEB | 22:00 | 22:15 | AFTER INSULATED NOW THERE IS NO LEAKAG |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 20:00 | 220260155 | 220260155 | 1 | AMC | AL FALAJ | ABU HAIL | SHJ | CHILLER NO.3 TEMP ISUUE | AHSAN |  | 21:00 | 0:00 | EVAPORATOR ICE FORMATION /AFTER REMOVE ICE NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 20:00 | 220260156 |  | 0 | AMC | CAREEM | MARINA | DXB | LIGHT ISSUE | SARVANAN | SHABEEB | 1:40 | 2:30 | CHANGED THE LIGHT NOW WORKING |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 21:00 | 220260157 | 220260157 | 1 | AMC | CAREEM | MARINA | DXB | CHILLER NO.9 WATER ISSUE ,FREEZER NO.4 NOS LIGHT NOT WORKING | SHABEEB | SARAVANAN | 1:40 | 2:30 | DRAIN BLOCK IN CHILLER CLEARD DRAIN ISSUE /FOR FREEZER NEED LIGHT TO BE CHANGE | NEED:- T 5 WHITE LIGHT - 4NOS , 220 V LED SET - 4 NOS |  | ATTENDED | NEED MATERIAL
2026-02-05 | 16:00 | 220260158 |  | 0 | AMC | ENOC | 1511 | SHJ | REPLACE COMPRESSOR | RACEL |  | 16:24 | 21:54 | REMOVED THE OLD COMPRESSOR AND INSTALLED NEW COMPRESSOR NOW WORKING NORMAL | USED :- REPLACED NEW COMPRESORE |  | COMPLETED | WORK COMPLETED
2026-02-05 | 21:00 | 220260159 |  | 0 | AMC | ENOC | 1060 | DXB | BED FREEZER NOT WORKING | SHABEEB | SARAVANAN | 23:00 | 1:30 | FOUND LEAKE BEFOR /NOW ARRESTED LEAK ISSUE NOW WORKING NORMAL | USED:- R 404 A -1NOS,BLUE ROD,SERVICE VALVE BY TD |  | COMPLETED | WORK COMPLETED
2026-02-05 | 20:00 | 220260160 |  | 0 | AMC | ENOC | 1056 | DXB | WALKIN FREEZER LIGHT ISSUE | SHABEEB | SARAVANAN | 3:00 | 3:30 | CHANGED THE HOLDER NOW WORKING NORMAL | HOLDER -220 - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-02-05 | 0:14 | 220260161 | 220260161 | 1 | AMC | NESTO | AJF | AJM | EGG CHILLER WATER LEAKAGE | AHSAN |  | 1:40 | 2:50 | FOUND MAIN DRAIN BLOCK FOR CHILLER TEMPORARY MAKE IT SOULUTION BUT NEED TO CLEAR MAIN LINE BLOCK |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 21:00 | 220260162 | 220260162 | 1 | AMC | NESTO | AJC | AJM | PPM | ABHIJITH | SUDHEESH | 22:30 | 0:00 | PPM DONE /CHECKED ALL UNITS UNDER OUR SCOOP IS WORKING NORMAL TEMPURATURE. |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 8:00 | 220260163 | 220260163 | 1 | AMC | HOP | JEBAL ALI | DXB | PPM | MUTHUKUMAR | SHAHABUDIN |  |  | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 8:00 | 220260164 | 220260164 | 1 |  |  | DRIVING | DXB | DRIVING | WILSON |  | 8:30 | 18:30 | DXB, WAREHUSE |  |  | COMPLETED | WORK COMPLETED
2026-02-05 | 20:00 | 220260165 | 220260165 | 1 | AMC | AMAZON | DXB 3 | DXB | PPM Q 1 | GOVIND/ABID | [6 empty] | COMPLETED | WORK COMPLETED
2026-02-06 | 8:00 | 220260166 |  | 0 | AMC | ENOC | 1401 | RAK | WALKIN FREEZER SHOUT DOWN | SABITH ALI |  | 10:30 | 12:15 | FOUND ICE FORMATION AND DRAIN PROBLEM /AFTER CLEAR ICE FORMATION AND DRAIN PAN CLEAND NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 8:00 | 220260167 | 220260152 | 2 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | TABLE CHILLER HIGH TEMP.ISSUE | TROVEE |  | 14:24 | 14:40 | FOUND COMPRESSER DAMAGE | NEED :- COMPRESSOR AND INSTALATION FITTINGS |  | ATTENDED | NEED MATERIAL
2026-02-06 | 8:11 | 220260168 | 220260168 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE ICE FALLING OUT SIDE | RANDOLPH | TROVEE | 8:20 | 8:51 | ICE FLAKS DRUM DEFACTED AFTER FIXING DRUM NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 8:11 | 220260169 | 220260169 | 1 | AMC | AD COOP/DEYAAR | MINA | AUH | CHILLER NOT WORKING NO 07 | RANDOLPH | TROVEE | 9:10 | 9:30 | FOUND SOLENOID VALVE COIL NOT WORKING DUE TO LOSS CONNECTION AFTER FIXING NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 9:00 | 220260170 | 120260087 | 2 | AMC | AD COOP/DEYAAR | MUROOR | AUH | CHEESE CHILLER STORAGES NOT WORKING PROPERLY | [6 empty] | ALREADY REQUESTED FOR REPLACE COMPRESSOR | ATTENDED | NEED MATERIAL
2026-02-06 | 11:00 | 220260171 | 220260171 | 2 | AMC | CAREEM | JADAFF | DXB | COLD ROOM DOOR GASKET | MOHAMMED |  | 16:10 | 16:55 | FOUND CURTAIN DAMAGE NEED TO REPLACE AIR CURTAIN | NEED:- 2 NOS AIR CURTAIN |  | ATTENDED | NEED MATERIAL
2026-02-06 | 8:00 | 220260172 | 220260172 | 1 | AMC | NESTO | SATWA | DXB | EGG PAROTTA CHILLER | SADAM |  | 9:20 | 11:00 | FOUND DRAIN BLOCK IN MAIN PIPE LINE NEED TO CLEAR WITH PLUMBER |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 9:00 | 220260173 | 220260173 | 1 | AMC | NESTO | KARAMA | DXB | COLD ROOM LIGHT NOT WORKING | SARVANAN |  | 22:30 | 22:45 | LIGHT IS DAMAGE NEED TO REPLACE | USED: 4 FEET LED LIGHT |  | COMPLETED | WORK COMPLETED
2026-02-06 | 11:40 | 220260174 | 220260174 | 1 | AMC | MAMZAR VILLA | DUBAI | DXB | FREEZER COLD ROOM NOT WORKING | SADAM |  | 11:45 | 17:00 | CONTROLER SHOWING ALARM FOUND ICE FORMATION IN EVAPORATOR AFTER CLEAN NOW NORMAL WORKING | IF NEXT TIME SAME ISSUE NEED TO BE CHANGE KP 15 SWITCH |  | COMPLETED | WORK COMPLETED
2026-02-06 | 11:40 | 220260175 | 220260175 | 2 | AMC | BANIYAS COOP | SHAHAMA | AUH | CHILLER TEMP ISSUE. | RANDOLPH | TROVEE/OLIVER | 13:30 | 13:51 | FOUND COMPRESSOR HIHG AMPHER NEED TO CHANGE | NEED:- COMPRESSOR AND INSTALLTION |  | ATTENDED | NEED MATERIAL
2026-02-06 | 11:40 | 220260176 | 220260176 | 1 | AMC | AD COOP/DEYAAR | MADINAT ZAYED | AUH | CHILLER LIGHT NOT WORKING | RANDOLPH | TROVEE/OLIVER | 12:20 | 12:52 | FOUND THAT ELECTRINIC BALLAST IS DAMAGE NEED TO REPLACE | NEED:- ELECTRONIC BALLAST |  | ATTENDED | NEED MATERIAL
2026-02-06 | 12:40 | 220260177 | 220260177 | 2 | AMC | NESTO | AJE | AJM | ICE MACHINE NOT WORKING | SABITH ALI | AHSAN | 18:20 | 21:15 | FOUND THE WATER PUMP BARING IN DEFECTIVE NEED TO REPLACE /AFTER GREESING WORKING NOW NORMAL | NEED:- BAERING |  | ATTENDED | NEED MATERIAL
2026-02-06 | 12:40 | 220260178 | 220260141 | 2 | AMC | NESTO | MALEHA | SHJ | SALAD COUNTER TEMP ISSUE. | SABITH ALI |  | 14:45 | 16:00 | COMPRESSOR IS OVER HEATING NEED TO CHARGE GAS AND CHANGE FILTER DRIER | NEED: 290 GAS - 1, FILTER DRIER-1/4, NITROGEN |  | ATTENDED | NEED MATERIAL
2026-02-06 | 1:40 | 220260179 | 220260179 | 1 | AMC | CAREEM | ARABIAN STORE | DXB | DRAIN PUMP WATER LEAKGE | [6 empty] | NEED PASS NO ENTRY | NOT ATTENDED | RESCHEDULE
2026-02-06 | 13:58 | 220260180 | 220260180 | 1 | AMC | AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | CONDENSOR FAN MOTOR NOT WORKING | TROVEE | OILIVER | 15:50 | 4:20 | FOUND ICE FORMATION SO FAN HAS STUCK AFTER REMOVE ICE NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 13:29 | 220260181 | 220260128 | 3 | AMC | BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER NO COOLING | DENNIS | RACEL | 17:12 | 20:35 | FOUND THE EVAPORATOR IS NOT IN POSITION NEED TO BE REPOSITION TO CORRECT AIR FLOW /AFTER DONE JOB NOW SYSTEM IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 9:00 | 220260182 |  | 0 | AMC | ENOC | 1047 | DXB | WLK IN FREEZER DRAIN LINE LEAKAG | MOHAMMED |  | 10:00 | 12:45 | FOUND THE LEAKAG FROM GRAIN LINE REMOVE THE DRAIN AFTER CLEAN FIXED NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 9:00 | 220260183 | 7100294827 | 2 | AMC | ENOC | 1205 | SHJ | WALK IN CHILLER LIGHT NOT WORKING | RACEL |  | 10:45 | 15:35 | FOUND 3 LIGHT BUSTED AFTER RE PLACE WORKING NORMAL. | USED:- 3 NOS LIGHT LED 220W-220V |  | COMPLETED | WORK COMPLETED
2026-02-06 | 9:00 | 220260184 |  | 0 | AMC | ENOC | 1205 | SHJ | DOOR BTTOM SIDE GASKET DAMAGE IN WALK IN FREEZER &LIGHT NOT WORKING | RACEL |  | 10:45 | 15:35 | REMOVE THE DOR AND RECTIFY THE ISSUE NOW DOOR OPENING NORMAL /NOW CHANGED LED 2 LIGHTS | USED - 2 LED LIGHTS |  | COMPLETED | WORK COMPLETED
2026-02-06 | 16:08 | 220260185 | 220260177 | 2 | AMC | NESTO | AJE | AJM | FISH SECTIONCHILLER NOT WORKING | SABITH ALI | AHSAN | 18:20 | 21:15 | FOUND THE WATER PUMP BARING IN DEFECTIVE NEED TO REPLACE /AFTER GREESING WORKING NOW NORMAL | NEED:- BAERING |  | ATTENDED | NEED MATERIAL
2026-02-06 | 9:57 | 220260186 | 220260186 | 1 | AMC | TCS | ROVE HEALTH CARE | DXB | WATER LEAKAGE FROM CHILLER | SARVANAN |  | 23:45 | 1:00 | FOUND THERE IS NOT HEATING PRIMERY OIL PROPER /AFTER GAS TOP UP NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 20:11 | 220260187 | 220260187 | 2 | AMC | AD COOP/DEYAAR | SE 13 | AUH | FREEER TEMP ISSUE. NO.1 | FROILAN | WILLIAM | 20:50 | 48:00 | FOUND LEAKAGE IN DISCHARGE SECTION NEED TO BRAZING AND CHARGE GAS | NEED:- 10 404 A CYLD |  | ATTENDED | NEED MATERIAL
2026-02-06 | 20:00 | 220260188 | 220260188 | 1 | AMC | AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | COMBI FREEZER TEMP ISSUE | FROILAN | WILLIAM | 1:11 | 2:23 | FOUND THER IS NO ISSUE TEMP IS NORMAL UNIT NOW UNDER OBSERVATION |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 20:20 | 220260189 | 220260189 | 1 | AMC | BAQER MOHEBI | AL NAHDA | SHJ | ISLAND FREEZER TRIPPING | AHSAN | ABHIJITH/SUDHEESH | 22:00 | 23:20 | FOUND THERE HEATERS NOT WORKING /WE DISCONECTED HEATER NEED TO REPLACE | NEED:- HEATERS - 6 PCS |  | ATTENDED | NEED MATERIAL
2026-02-06 | 23:34 | 220260190 | 220260190 | 2 | AMC | RNQ | AJMAN | AJM | COLD ROOM TEMP. ISSUE | VIGNESH | [6 empty] | NOT ATTENDED | RESCHEDULE | ON 7/2/2026
2026-02-06 | 23:00 | 220260191 | 120260426 | 2 | AMC | ANSAR | KARAMA | DXB | WATER LEAK FROM FREEZER | AHSAN | ABHIJITH/SUDHEESH | 0:00 | 3:10 | CHANGED THE INSULATION BUT NEED DRAIN FITTINGS | NEED:UPV FITTING AND COLLING FAN 120 X 120 - 4 NOS |  | ATTENDED | NEED MATERIAL
2026-02-06 | 8:00 | 220260192 |  | 0 | AMC | ENOC | 1083 | DXB | PPM | MUTHUKUMAR | SHAHABUDIN/ZALAUDDIN |  |  | PPM DON Q 4 |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 8:00 | 220260193 |  | 0 | AMC | ENOC | 1092 | DXB | PPM | MUTHUKUMAR | SHAHABUDIN/ZALAUDDIN |  |  | PPM DON Q 4 |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 8:00 | 220260194 | 7100295791 | 1 | AMC | ENOC | 1086 | DXB | VERTICAL FREEZER NOT WORKING | SARVANAN |  | 20:40 | 8:50 | FOUND UNIT IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-06 | 8:00 | 220260195 | 7100294782 | 1 | AMC | ENOC | 1088 | DXB | WALKIN FREEZER NO GAS KET | SARVANAN |  | 1:35 | 1:50 | NEED TO CHANGE GASKET | NEED:- GASKET- 97 X 192CM |  | ATTENDED | NEED MATERIAL
2026-02-06 | 7:00 | 220260196 |  | 0 | AMC |  | DRIVING | DXB | DRIVING | WILSON |  | 7:20 | 19:40 | DXB,AJMAN |  |  | COMPLETED | WORK COMPLETED
2026-02-06 |  | 220260197 | 220260197 | 2 | AMC | GOURMET | 1004 AL REEM | AUH | PPM / MARKET AREA | FROILAN | WILLIAM |  |  | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-06 |  | 220260198 | 220260197 | 2 | AMC | GOURMET | 1004 AL REEM | AUH | PPM / KITCHEN AREA | FROILAN | WILLIAM |  |  | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-06 |  | 220260199 | 220260199 | 1 | AMC | NESTO | AJC | AUH | ICE MACHINE ISSUE | AHSAN | ABHIJITH/SUDHEESH | 4:00 | 4:45 | CHECK ALL COMPONENTS AND WATER LEVEL ARE WORKING NORMAL SYSTEM UNDER OBSERVATION |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 8:00 | 220260200 | 220260190 | 2 | AMC | RNQ | AJMAN | AJM | COLD ROOM TEMP. ISSUE | VIGNESH |  | 9:00 | 11:25 | FOUND THE INDOOR CONTACTOR DAMAGE AFTER REPLACE WORKING NORMAL | USED: LC1D25 - 1NOS |  | COMPLETED | WORK COMPLETED
2026-02-07 | 8:00 | 220260201 | 220260201 | 1 | AMC | BANYA FOREST | DUBAI | DXB | KITCHRN AC ISSUE | ABUTAKHIR | [6 empty] | ATTENDED | ATTENDED
2026-02-07 | 8:00 | 220260202 | 220260202 | 2 | AMC | LULU | MAQAM | AL AIN | CHEESE DISPLAY CHILLER LIGHT NOT WOTKING | TALIB |  | 17:55 | 18:30 | FOUND THE LIGHT WIRE HAS BROKEN NEED TO REPAIR | NEED: NEED LIGHT REPAIR |  | ATTENDED | ATTEND ON 8/2/2026
2026-02-07 | 8:00 | 220260203 | 7100295931 | 1 | AMC | ENOC | 4009 | DXB | WATER LEAKAGE | SABITH ALI |  | 10:45 | 11:50 | FOUND DRAIN PIPE LINE BLOCK AFTER CLEAN NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 10:17 | 220260204 |  | 0 | AMC | ENOC | 1035 | DXB | CHILLER AND FREEZER ISSUES | MOHAMMED |  | 11:00 | 14:00 | FOUND FREEZER ROOM DRAIN PIPE DISCONECTED AFTER CONNECT NOW OK BUT FOR CHILLER NEE INSULATION FOR FIX PROBLEM | NEED:- 7/8 INSULATION - 1 NOS ARO FOAM -2 NOS, SILICON - 1 NOS, BLACK TAP-2 NOS. |  | ATTENDED | NEED MATERIAL
2026-02-07 | 8:16 | 220260205 | 220260205 | 1 | AMC | AD COOP/DEYAAR | MBZ | AUH | FREEZER NOT WORKING | RANDOPLH | OLIVER/TROVEE | 9:10 | 10:15 | FOUND ICE BLOCK DRAIN AFTER CLEAN ICE NOW SUNIT IS NORMAL WORKING |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 10:37 | 220260206 | 220260206 | 1 | AMC | AD COOP/DEYAAR | ABU DHABI | AUH | COMPRESSOR TRIPPING | RANDOPLH | OLIVER/TROVEE | 12:45 | 13:33 | FOUND THE TIMMING RELAY DEFECTED NEED TO REPLACE | NEED:- TIMMING RELAY - 4 NOS |  | ATTENDED | NEED MATERIAL
2026-02-07 | 9:21 | 220260207 | 220260207 | 2 | AMC | NESTO | SATWA | DXB | BUTCHERY SECTION TEMP ISSUE | AHSAN | ABHIJITH/SUDHEESH | 23:00 | 2:30 | IN SALAD UNIT FOUND LESS GAS BUT NO SING FOR LEAK AFTER CHARGE GAS NOW WORKING NORMAL & BUTCHERY SECTION REMOVED THE ICE FORMATION IN CONDENSOR AND RESET SETTINGS |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 9:31 | 220260208 | 220260208 | 1 | AMC | NESTO | AJC | AJM | CHILLER COLD ROOM NOT WORKING AND ICE MACHINE | SABITH ALI |  | 13:10 | 14:55 | FOUND OUT ICE MACHINE ARE WORKING NORMAL IN COLD ROOM INSIDE LIGHT NOT WORKING | USED:- LED LIGHT 4 FEET - 2 NOS |  | COMPLETED | WORK COMPLETED
2026-02-07 | 12:10 | 220260209 | 220260209 | 1 | AMC | CAREEM | AL WASL | DXB | NEED TO CLEAN PPM | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-07 | 12:37 | 220260210 | 220260210 | 1 | AMC | PASSONS | FUJEIRAH | FUJ | DELI CHILLER TRIPPING | VIGNESH |  | 20:15 | 18:30 | ICE FORMATION IN FAN MOTOR IN THAT CAUSE IS TRIPPING AFTER REMOVE ICE FORMATION NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 1:00 | 220260211 | 7100297163 | 2 | AMC | ENOC | 1507 | FUJ | WALKIN CHILLER TEMP ABNORMAL | VIGNESH |  | 12:40 | 14:00 | FOUND CONDECTOR DAMAGE AFTER CHANGE CONTECTOR NOW NORMAL WORKING | USED:- LC1D32M7 - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-02-07 | 1:00 | 220260212 | 220260212 | 1 | AMC | GRANDIOSE | AL WASL | DXB | MEET FREEZER TEMP.ISSUE | MOHAMMED |  | 15:55 | 19:05 | FOUND ICE FORMATION ADTER CLEAR IC CHECKED FOR LEAK THERE IS NO SING FOR LEAKAGE AFTER TOP UP GAS SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 1:46 | 220260213 | 220260213 | 1 | AMC | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | CHEESE COUNTER CHILLER IS NOT WORKING | AHSAN | ABHIJITH/SUDHEESH | 3:00 | 3:50 | FOUND THE LOW GAS AFTER GAS CHARGE WORKING NORMAL | USED R 404 - 1 NOS BY STORE |  | COMPLETED | WORK COMPLETED
2026-02-07 | 1:57 | 220260214 | 220260187 | 2 | AMC | AD COOP/DEYAAR | SE 13 | AUH | GAS CHARGING | RANDOLPH | TROVEE | 15:10 | 17:15 | FOUND GAS IN STORE AFTER CHARE GAS NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 12:00 | 220260215 | 220260215 | 1 | AMC | NESTO | SATWA | DXB | SALAD SECTION TEMP ISSUE | AHSAN | ABHIJITH/SUDHEESH | 23:00 | 2:30 | IN SALAD UNIT FOUND LESS GAS BUT NO SING FOR LEAK AFTER CHARGE GAS NOW WORKING NORMAL & BUTCHERY SECTION REMOVED THE ICE FORMATION IN CONDENSOR AND RESET SETTINGS |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 11:36 | 220260216 | 220260216 | 1 | AMC | NESTO | FUJEIRAH | FUJ | FREEZER WATER LEAK | VIGNESH |  | 18:35 | 19:00 | FOUND THERE IS NO ANY WATER LEAKAGE |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 11:00 | 220260217 | 7100295805 | 1 | AMC | ENOC | 1203 | SHJ | PRONTO SECTION TABLE CHILLER NOT WORKING | SABITH ALI |  | 15:50 | 16:10 | FOUNDED CHILLER IS NOT OUR SCOOP |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 8:00 | 220260218 | 220260218 | 1 | AMC | NESTO | AL AIN | AL AIN | RECHARGE GAS 10 NOS | TALIB |  | 11:35 | 17:10 | CHARGED GASFROM TD STOCK | USED:- 10 CYLD 404 |  | COMPLETED | WORK COMPLETED
2026-02-07 | 8:00 | 220260219 |  | 0 | AMC | ENOC | 1666 | DXB | PPM | MUTHUKUMAR | SHANOJ/ZALAUDDIN/KADAR |  |  | PPM Q 4 DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 8:00 | 220260220 |  | 0 | AMC | ENOC | 1011 | DXB | PPM | MUTHUKUMAR | SHANOJ/ZALAUDDIN/KADAR |  |  | PPM Q 4 DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 17:00 | 220260221 |  | 0 | AMC | GOURMET | 1004 AL REEM | DXB | CONDENSOR FAN MOTOR NOT WORKING | FROILAN | OLIVER | 18:35 | 20:35 | DONE CHANGING CONDENSORE FAN MOTOR | USED:- CONDENSORE FAN MOTOR 16 X-3NOS,FAN BLADE,FAN HOLDER |  | COMPLETED | WORK COMPLETED
2026-02-07 | 18:30 | 220260222 | 220260222 | 2 | AMC | CAREEM | AL WASL | DXB | FREEZER COLD ROOM NOT WORKING | AHSAN | ABHIJITH/SUDHEESH | 19:30 | 21:10 | CHECK THE FREEZER COLD ROOM NORMAL WORKING BUT THE ITEMS IS LOADING SO TEMP. NOT REACHING NEED TO OBSERV AFTER LOADING |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 21:00 | 220260223 | 220260223 | 1 | AMC | LULU | OUD METHA | DXB | BUTCHERY DISPLAY HIGH TEMP & VEG CHILLER WATER LEAK | SARVANAN | SHABEEB | 22:00 | 0:00 | IN BUTCHERY SECTION FOUND LESS GAS BUT NO SING FOR LEAK AFTER CHARGE GAS NOW WORKING & VEG CHILLER DRAIN TRAY IS CLEAND NOW OK |  | DRAIN TRAY ONE SIDE BOTTOM DAMAGE | COMPLETED | WORK COMPLETED
2026-02-07 | 2:00 | 220260224 | 220260222 | 2 | AMC | CAREEM | AL WASL | DXB | FREEZER COLD ROOM NOT WORKING | SARVANAN | SHABEEB | 2:00 | 2:50 | CHECKED THE FREEZER COLD ROOM NOW TEMP AND GAS PRUSSER IS NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 12:00 | 220260225 | 220260225 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER NO.4 NOT WORKING | FROILAN | OLIVER | 15:03 | 17:47 | FOUND ICE FORMATION IN EAVAPORATOR AFTER REMPVE ICE CHECK DEFROST HEATER IS DAMAGE NEED TO REPLACE | NEED:- DEFROST HEATER |  | COMPLETED | WORK COMPLETED
2026-02-07 | 14:00 | 220260226 | 220260226 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | PLUGE IN DISPLAY CHILLER SHOWING ALARM | FROILAN | OLIVER | 17:00 | 17:30 | CHECK CONTROLLER IS DEFFECTED NEED TO CHANGE | NEED:- CONTROLLER DIXELL XR06CX WITH SENSOR , AND MAGNATIC CONTROLER |  | ATTENDED | NEED MATERIAL
2026-02-07 | 18:30 | 220260227 | 220260227 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | CHEESE PROMOTION CHILLER HIGH TEMP | RANDOLPH | TROVEE | 19:00 | 19:38 | CHARGE THE GAS FROM STORE NOW UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 18:30 | 220260228 | 220260228 | 1 | AMC | AD COOP/DEYAAR | KHALIDIYA GARDEN | AUH | BAKERY CHILLER WATER LEAKAGE 1 & 2 NO CHILLER | RANDOLPH | TROVEE | 19:49 | 20:10 | FOUND THE DRAIN PAN FULL SO REMOVE THE WATER FROM VACCUM NOW FUNTIONING IS OK |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 17:00 | 220260229 | 7100295795 | 1 | AMC | ENOC | 1143 | SHJ | OPEN CHILLER CBINET WATER LEAKAGE | SABITH ALI |  | 18:10 | 18:35 | FOUND MAIN DRAIN BLOCK FOR CHILLER NEED TO CLEAR MAIN LINE BLOCK |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 16:00 | 220260230 | 7100296076 | 1 | AMC | ENOC | 1077 | DXB | WALK IN FREEZER ICE FORMATION | SARVANAN | SHABEEB | 19:20 | 21:15 | FOUND THE DRAIN HEATER IS DAMAGE IN THE CAUSE THERE IS A ICE FORMATION AFTER REMOVE ICE CHANGE THE HEATER | USED:- COPPER PIPE HEATER- 3MTR BY TD |  | COMPLETED | WORK COMPLETED
2026-02-07 | 16:00 | 220260231 | 7100296042 | 1 | AMC | ENOC | 1022 | DXB | WALK IN CHILLER WATER LEAKAGE ISSUE | SARVANAN | SHABEEB | 1:20 | 1:30 | FOUND DRAIN DRAY PROPER NOT FIXING /AFTER FIXING TRAY NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 16:00 | 220260232 | 7100296062 | 1 | AMC | ENOC | 1074 | DXB | WALK IN FREEZER DOOR ICE FORMATION | SARVANAN | SHABEEB | 3:15 | 96:00 | AFTER ICE REMOVE CHECKED THERE IS NO AIR CURTIN WE FIXED THE AIR CURTIN | USED- AIR CURTIEN - 2 NOS |  | COMPLETED | WORK COMPLETED
2026-02-07 | 8:00 | 220260233 | 220260232 | 1 | AMC |  | DRIVING | DXB | DRIVING | WILSON |  | 8:30 | 6:30 | DXB MATERIAL ARRANGMENT |  |  | COMPLETED | WORK COMPLETED
2026-02-07 | 8:00 | 220260234 | 220260234 | 1 | AMC | AMAZON | DXB 3 | DXB | PPM Q 1 | ABID | GOVIND |  |  | PPM Q 1 DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-08 | 10:30 | 220260235 | 220260235 | 1 | AMC | LULU | AL WATHBA | AUH | SMELL ISSUE AND WATER LEAKAGE | FROILAN | OLIVER/WILLOM | 12:05 | 1:10 | FOUND MILK FELL DOWN IN DRAIN PAN AND DRAIN BLOCK /AFTER CLEANING SUCH THINGS NOW THERE IS NO SMELL ISSUE |  |  | COMPLETED | WORK COMPLETED
2026-02-08 | 10:30 | 220260236 | 220260236 | 1 | AMC | LULU | MAQAM | AL AIN | COLD ROOM LOCK ISSUE | TALIB |  | 13:00 | 14:00 | CHECKED THE DOOR LOCK IS NOT WORKINIG PROPERLY NED TO REPLACE | NEED: DOOR LOCK SET - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-08 | 8:39 | 220260237 | 220260237 | 1 | AMC | ENOC | 4037 | DXB | OPEN CHILLER WATER LEAKAG | SARAVANAN | SHABEEB | 21:55 | 23:55 | FOUND LEAK FROM PRIMARY COIL AND EVAPORATOR AFTER LEAK ARREST SVACCUM AND GAS CHARGR NOW SYSTEM WORKING NORMAL | USED:- R404 A - 1 NOS, BLUE ROD 2 NOS |  | COMPLETED | WORK COMPLETED
2026-02-08 | 9:53 | 220260238 | 220260238 | 1 | AMC | AD COOP/DEYAAR | SPAR ELECTRA | AUH | FREEZER ICE FORMATION | FROILAN | OLIVER/WILLOM | 10:30 | 11:32 | FOUND AIR FLOW IN OUTER AFTER APPLY SILLICON NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-08 | 7:58 | 220260239 | 220260239 | 3 | AMC | NESTO | AL MINA | DXB | WATER LEAKAGE | SADAM | MUTHUKUMAR | 8:50 | 11:45 | FOUND MOUISTER IN BODY AND PIPE LINE NEED FAN TO SOLUTION FOR STOP DRAIN LEAKAG | NEED:- FAN 80 X80 - 15NOS AND CABLE 20 MTR |  | ATTENDED | NEED MATERIAL
2026-02-08 | 9:48 | 220260240 | 220260240 | 1 | AMC | NESTO | KARAMA | DXB | CHEESE UNIT TEMP ISSUE FREEZER NO 4 ,5 | SADAM | MUTHUKUMAR | 12:15 | 16:30 | FOUD ICE FORMATION AND IN FREEZER NO 5 FAN MOTOR DAMAGR WHICH IS WE REPLACED | USED :- 10 W FAN MOTOR - 1 NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-02-08 | 15:09 | 220260241 | 220260241 | 1 | AMC | AD COOP/DEYAAR | SPAR SAADIAYT | AUH | CHEESE SECTION CHILLER TEMP ISSUE | FROILAN | OLIVER/WILLOM | 15:45 | 16:35 | FOUND GAS LOW AFTER CHARGE GAS SYSTEM NOW WORKING NORMAL PUT EXTRA DEFROST TO THE SYSTEM NOW UNDER OBSERVATION | USED 134 - 1 KG BY TD |  | COMPLETED | WORK COMPLETED
2026-02-08 | 12:47 | 220260242 | 220260207 | 2 | AMC | NESTO | SATWA | DXB | BUTCHERY SECTION CHILLER TEMP .ISSUE | RACEL |  | 14:15 | 20:15 | FOUND LEAK FROM ACCESS VALVE GAS IS LESS NEED TO BE CHARGE GAS | NEED:- 10 404 A CYLD |  | ATTENDED | NEED MATERIAL
2026-02-08 | 13:04 | 220260243 | 220260239 | 3 | AMC | NESTO | AL MINA | DXB | WATER LEAKAGE | SADAM | [6 empty] | ATTENDED | NEED MATERIAL
2026-02-08 | 14:49 | 220260244 | 220260244 | 1 | AMC | TCS | UMS | DXB | BACK STORE ROOM TEMP. ISSUE | VIGNESH |  | 15:30 | 19:00 | FOUND COIL SENSOR DAMAGE SO NEED TO REPLACE NEW SENSOR | USED:- NTC SENSOR - 1NOS, 2.5 X 4CR RR CABLE - 4 MTR |  | COMPLETED | WORK COMPLETED
2026-02-08 | 10:00 | 220260245 | 220260202 | 2 | AMC | LULU | MAQAM | AL AIN | CHEESE DISPLAY CHILLER LIGHT NOT WOTKING | TALIB |  | 13:00 | 14:00 | FOUND THE LIGHT WIRE HAS BROKEN NEED TO REPAIR | USED: AFTER LIGHT REPAIR |  | COMPLETED | WORK COMPLETED
2026-02-08 | 16:56 | 220260246 | 220260246 | 1 | AMC | AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | WATER LEAKAGE IN FREEZER | FROILAN | OLIVER/WILLOM | 18:00 | 18:25 | FOUND TRIPPING ISSUE NEED TO CHANGE FAN MOTOR AND SOME BUSTED LIGHT | NEED:- BOX FAN 120 X 120 - 1 NOS , LED LIGHT 2 FT - 15 NOS |  | ATTENDED | NEED MATERIAL
2026-02-08 | 20:33 | 220260247 | 219857 | 1 | AMC | ENOC | 1081 | DXB | WALK IN CHILLER HIGH TEMP | SARVANAN | SHABEEB | 1:00 | 2:15 | FOUND GAS LOW AFTER CHARGE GAS SYSTEM NOW WORKING NORMAL | USED - 404 A |  | COMPLETED | WORK COMPLETED
2026-02-08 | 20:33 | 220260248 | 7100295941 | 1 | AMC | ENOC | 1082 | DXB | PRONTO CHILLER LIGHT NOT WORKING | SARVANAN | SHABEEB | 2:45 | 3:45 | FOUND LIGHT BUSTED AFTER CHANGE GAS WORKING NORMAL | USED:- T8 2 FEET LED LIGHT - 4 NOS |  | COMPLETED | WORK COMPLETED
2026-02-08 | 16:41 | 220260249 | 220260249 | 2 | AMC | CAREEM | JVT | DXB | FREEZER COLD ROOM NOT WORKING | SADAM | MUTHUKUMAR | 18:00 | 19:35 | FOUND LOW GAS /AFTER GAS CHARGE NOW WORKING NORMAL | USED:- 404 - 3 KG BY TD |  | COMPLETED | WORK COMPLETED
2026-02-09 | 8:14 | 220260250 | 220260509 | 2 | AMC | AD COOP/DEYAAR | MUROOR | AUH | FAN MOTOR CHANGE | RANDOLPH | TROVEE | 9:39 | 10:16 | CHANGED THE FAN MOTOR 10- 25,25-40 COLD ROOM NOW BACK TO NORMAL | USED:- FAN MOTOR 10- 25,25-40 BY DEYAAR |  | COMPLETED | WORK COMPLETED
2026-02-09 | 8:52 | 220260251 | 220260251 | 1 | AMC | AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | BUTCHERY CHILLER NOT WORKING | FROILAN | OLIVER | 9:15 | 10:25 | FOUND THE CONTROLLER IS NOT FUNTION DUE TO THE PCB BOARD IS DAMAGE /AFTER MODIFIED THE ELECTRICAL OF THE REFRIGATION CONTROLLER NOW FREEZER IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 9:10 | 220260252 | 220260252 | 2 | AMC | AD COOP/DEYAAR | SPAR EXPRESS OMEGA TOWER | AUH | VEGETABLE CHILLER MAKING SOUND | RANDOLPH | TROVEE | 10:35 | 10:52 | CHECKED THE UNIT FOUND THE CONDENSORE FAN MOTOR HAS DAMAGED NEED TO REPLACE | NEED:- FAN MOTOR 16-25 - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-09 | 6:44 | 220260253 |  | 0 | AMC | ENOC | 1030 | DXB | WALK IN CHILLER HIGH TEMP | SADAM | ZALAUDIN | 8:30 | 10:00 | FOUND LOW GAS /AFTER GAS CHARGE NOW WORKING NORMAL | USED:- R 404 A - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-02-09 | 8:05 | 220260254 |  | 0 | AMC | ENOC | 1074 | DXB | WALKIN FREEZER DOOR ISUUE, CANT OPEN | SADAM | ZALAUDIN | 11:15 | 11:50 | FOUND DOOR STUCK WITH PLASTIC STRIP | NEED GASKET -2 MTR |  | ATTENDED | NEED MATERIAL
2026-02-09 | 10:19 | 220260255 | 7100296455 | 2 | AMC | ENOC | 1205 | DXB | Walk in Freezer ice formation | VIGNESH | AHSAN | 10:30 | 15:00 | FOUND EVAPORATOR FAN MOTOR DAMAGE AND DRAIN HEATER NOT WORKING /AFTER CHANGING SPARE PARTS NOW WORKING NORMAL | USED:- 10 W FAN MOTOR - 1NOS,DRAIN HEATER -2MTR - 1 NOS. |  | COMPLETED | WORK COMPLETED
2026-02-09 | 6:00 | 220260256 | 220260079 | 4 | AMC | GRANDIOSE | SOUQ AL BAHAR | DXB | NEED TO CHECK COMPRESSOR | SADAM | ZALAUDIN | 6:25 | 7:10 | FOUND UNIT COMPRESSOR HAS GROUNDED NEED TO CHANGE AND ALSO NEED TO REPLACE DOOR GASKET | NEED - COMPRESSOR AND INSTALATION MATIREALS AND DOOR GAS KET |  | ATTENDED | NEED MATERIAL
2026-02-09 | 10:51 | 220260257 | 220260257 | 1 | AMC | CAREEM | JVC PLAZA | DXB | CHILLER HIGH TEMP. ISSUE | VIGNESH |  | 16:35 | 17:25 | FOUND COMPRESSORE HAS DAMAGE | NEED:- COMPRESSOR AND INSTALATION MATIREALS |  | ATTENDED | NEED MATERIAL
2026-02-09 | 11:12 | 220260258 | 220260258 | 1 | AMC | BANIYAS COOP | BANIYAS CENTER | AUH | UNIT HIGH TEMP. | FROILAN | OLIVER | 15:00 | 15:30 | FOUND THE COMPRESSOR MACHANICAL FAILURE | NEED:- COMPRESSOR AND INSTALLTION MATIREALS |  | ATTENDED | NEED MATERIAL
2026-02-09 | 10:50 | 220260259 | 7100296257 | 3 | AMC | ENOC | 4014 | DXB | WATER LEAKAGE | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-09 | 8:19 | 220260260 | 220260260 | 2 | AMC | NESTO | AJE | AJM | ICE MACHINE DAMAGE | AHSAN |  | 9:30 | 12:42 | FOUND THE PROBLEM IN WATER PUMP NEED TO CHANGE | NEED:- WATER PUMP |  | ATTENDED | NEED MATERIAL
2026-02-09 | 8:19 | 220260261 | 220260261 | 1 | AMC | NESTO | FUJEIRAH | FUJ | WATER LEAKAGE | RACEL |  | 10:30 | 14:20 | FOUND THE WATER LEAK FROM DRINE PIPE NOT FIXED PROPER /AFTER FIXING DRAIN LINE AND APPLIED SILLICON NOW THERE IS NO LEAK SING |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 9:00 | 220260262 | 220260239 | 3 | AMC | NESTO | AL MINA | DXB | WATER LEAKAGE | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-09 | 1:20 | 220260263 | 220260263 | 1 | AMC | NESTO | AJL | AJM | FREEZER NOT WORKING | AHSAN |  | 15:00 | 17:40 | FOUND THE CONDENSOR BLOCK AFTER CLEANING CONDENSOR AND CHANGING TEMP SETTINGS NOW SYSTEM IS WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 12:06 | 220260264 | 220260264 | 1 | AMC | CAREEM | CITY LAND | DXB | FREEZER HIGHT TEMP. | SADAM |  | 14:15 | 16:20 | FOUND EVAPORATOR FANS NOT WORKING LIMIT SWITCH IS DAMAGED / AFTER CHANGE LIMIT SWITCH NOW WORKING NORMAL | USED:- LIMIT SWITCH |  | COMPLETED | WORK COMPLETED
2026-02-09 | 11:46 | 220260265 | 7100296219 | 1 | AMC | ENOC | 1143 | SHJ | Open Chiller Drainage blocked | RACEL |  | 15:50 | 17:25 | FOUND MAIN DRAIN LINE IS BLOCK /AFTER FLUSHING NOW DRAIN IS FREE |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 11:46 | 220260266 | 7100296257 | 3 | AMC | ENOC | 4014 | DXB | water leaking in the chiller | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-09 | 11:46 | 220260267 | 7100296281 | 2 | AMC | ENOC | 1057 | DXB | walk in chiller temp is breakdown | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-09 | 11:46 | 220260268 | 7100296296 | 2 | AMC | ENOC | 1099 | DXB | C-store Chiller Display Shelves Repaint | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-09 | 11:46 | 220260269 | 7100296307 | 1 | AMC | ENOC | 1013 | DXB | WALK IN CHILLER TEMPERATURE | SHABEEB |  | 1:05 | 2:25 | FOUND THE GAS LEVEL LOW CHEKED FOR LEAK BUT THERE IS NO LEAK /AFTER CHARGING GAS NOW WORKING NORMAL | USED:- GAS 404 - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-02-09 | 11:46 | 220260270 | 7100296309 | 1 | AMC | ENOC | 1044 | DXB | Walking freezer door not closing proper | SHABEEB |  | 3:00 | 4:40 | FOUND ICE FORMATION IN DOOR AFTER CLEAN ICE NOW DOOR IS WORKING |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 11:46 | 220260271 | 7100296388 | 1 | AMC | ENOC | 1044 | DXB | Ice forming at walking freezer. | SHABEEB |  | 3:00 | 4:40 | ICE FORMATION BECOUSE OF DOOR NOT CLOSING PROPERLY NOW WORKING OKAY |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 11:46 | 220260272 | 7100296455 | 2 | AMC | ENOC | 1205 | DXB | Walk in Freezer ice formation | VIGNESH | AHSAN | 10:30 | 15:00 | FOUND EVAPORATOR FAN MOTOR DAMAGE AND DRAIN HEATER NOT WORKING /AFTER CHANGING SPARE PARTS NOW WORKING NORMAL | USED:- 10 W FAN MOTOR - 1NOS,DRAIN HEATER -2MTR - 1 NOS. |  | COMPLETED | WORK COMPLETED
2026-02-09 | 2:10 | 220260273 | 220260273 | 1 | AMC | LULU | MAQAM | AL AIN | CHILLER COLD ROOM BURNING SMELL ISSUE. | TALIB |  | 14:35 | 17:15 | FOUND THE EVAPORATOR FAN NOT WORKING SMELL IS BURNING FAN MOTOR | NEED:- FAN MOTO RVRC2L3A2SC.1 - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-09 | 8:00 | 220260274 | 220260060 | 3 | AMC | NESTO | AJE | AJM | HOT CABIN ISSUE. | AHSAN |  | 9:20 | 12:40 | CHANGED THE ONE HEATER OTHER ONE WILL CHANGE LATER AS PER COUSTEMER NOW RUSH TIME |  | STILL ONE HEATER PENDING TO INSTALL | COMPLETED | WORK COMPLETED
2026-02-09 | 9:00 | 220260275 | 220260275 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE NOT WORKING. ICE FALLING OUT SIDE | OLIVER | FROILAN | 11:40 | 13:00 | FOUND THE ICE MACHINE OUTLET PIPE IS DAMAGE AFTER REPAIRE NOE WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 8:00 | 220260276 | 220260171 | 2 | AMC | CAREEM | JADAFF | AUH | COLD ROOM DOOR GASKET | MOHAMMED | ZALAUDIN | 10:15 | 10:45 | REMOVED OLD AIR CURTIN AND FIXED NEW | USED:- AIR CURTIN - 2 NOS |  | COMPLETED | WORK COMPLETED
2026-02-09 | 8:00 | 220260277 | 120260428 | 2 | AMC | NESTO | AL FAHIDI | DXB | ICE FORMATION | MOHAMMED | ZALAUDIN | 11:00 | 15:45 | REPLACED THE CONTROLLER 2 02 D WITH SENSOR AND CONTACTOR | USED:- DANFOSS CONTROLLER , PT 100 SENSOR - 2 NOS |  | COMPLETED | WORK COMPLETED
2026-02-09 | 3:22 | 220260278 | 220260249 | 2 | AMC | CAREEM | JVT | DXB | FREEZER COLD ROOM NOT WORKING | VIGNESH/MOHAMMED | ZALAUDIN | 17:15 | 20:15 | FOUND THE LEAKAG IN ELBOW AFTER MAKING WELDING NOW SYSTEM WORKING NORMAL | USED:- 404 A - 1NOS |  | COMPLETED | WORK COMPLETED
2026-02-09 | 17:24 | 220260279 | 220260279 | 1 | AMC | CAREEM | BB2 | DXB | FREEZER HIGHT TEMP. | SHABEEB |  | 21:41 | 22:30 | FOUND LOSE CONNECTION IN POWER SOCKET AFTER REPAIR NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 16:42 | 220260280 |  | 0 | AMC | ENOC | 1161 | SHJ | PRONTO VERTICAL FREEZER HIGH TEMP. | AHSAN |  | 18:35 | 22:00 | FOUND THE EVAPORATORE ICE FORMATION /AFTER REMOVE ICE NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 16:42 | 220260281 | 220260252 | 2 | AMC | AD COOP/DEYAAR | SPAR EXPRESS OMEGA TOWER | AUH | VEGETABLE CHILLER MAKING SOUND /FAN CHANGING | RANDOLPH | OLIVER/FROILAN | 17:00 | 17:25 | CHANGED THE FAN MOTORE NOW SYSTEM BACK TO NORMAL | USED:- FAN MOTOR 16 - 25 - 1 NOS BY DEYAAR |  | COMPLETED | WORK COMPLETED
2026-02-09 | 14:49 | 220260282 | 220260282 | 2 | AMC | NESTO | WAREHOUSE | DXB | COLD ROOM DOOR ISSUE | SHABEEB |  | 23:35 | 0:00 | FOUND THE DOOR HANDEL PROBLEM NEED TO REPLACE | NEED:- COLD ROOM DOOR HANDEL |  | ATTENDED | NEED MATERIAL
2026-02-09 | 20:00 | 220260283 | 220260283 | 1 | AMC | BAQER MOHEBI | ABU HAIL | SHJ | COMBI FREEZER TEMP ISSUE | SABITH ALI | ABHIJITH/SUDHEESH | 20:30 | 23:40 | FOUND THE ICE FORMATION IN EVAPORATOR AFTER REMOVE ICE WORKING NORMAL /IDENTIFY NEED ONE MORE HEATER | NEED:- HEATER - 340CM - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-09 | 20:17 | 220260284 | 220260284 | 2 | AMC | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | WATER LEAKAGE | [7 empty] | ATTENDED | ATTEND ON 10/2/2026
2026-02-09 | 8:00 | 220260285 |  | 0 | AMC | ENOC | 1039 | DXB | PPM | MUTHUKUMAR | SHANOJ /KADDER |  |  | PPM Q 4 DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-09 | 8:00 | 220260286 |  | 0 | AMC | ENOC | 1029 | DXB | PPM | MUTHUKUMAR | SHANOJ /KADDER |  |  | PPM Q 4 DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 6:10 | 220260287 | 220260287 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | WATER LEKAGE AT MILK CHILLER C-4 | FROILAN | OLIVER/WILLOM | 9:13 | 9:54 | FOUND THE DRAIN HEATER IS DAMAGE IN THE CAUSE THERE IS A DRAIN LEAK | NEED:- DRAIN PAN HEATER - 330 WATS |  | ATTENDED | NEED MATERIAL
2026-02-10 | 9:02 | 220260288 | 220260288 | 1 | AMC | AD COOP/DEYAAR | ZAYED 1ST | AUH | BUTCHERY CHILLER NOT WORKING | FROILAN | OLIVER/WILLOM | 10:18 | 11:18 | FOUND ICE FORMATION IN THE EVAPURETUR /AFTER REMOVING ICE UNIT WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 6:26 | 220260289 | 7100296586 | 1 | AMC | ENOC | 1126 |  | vertical freezer not working | VIGNESH | SELVAN | 12:40 | 15:00 | FOUND LOW GAS /AFTER GAS CHARGE NOW WORKING NORMAL | USED: 290 - 1 KG |  | COMPLETED | WORK COMPLETED
2026-02-10 | 6:26 | 220260290 | 7100296627 | 1 | AMC | ENOC | 1125 |  | Walk in freezer not working. | VIGNESH | SELVAN | 8:40 | 12:00 | FOUND THE TRIPPING ISSUE THE BRAKER HAS DAMAGE /AFTER BRAKER CHANGED NOW WORKING NORMAL | USED:- MCB 3 POLE BRAKER -32A - 1 NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-02-10 | 6:26 | 220260291 | 7100296573 | 1 | AMC | ENOC | 1074 | DXB | Walk in freezer door hard to open | MUSTAFA |  | 13:24 | 14:50 | FOUND BOTTOM GASKET HAS DAMAGED/AFTER REPLACED NEW GASKET NOW WORKING NORMAL | USED:- GASKET - 2MTR |  | COMPLETED | WORK COMPLETED
2026-02-10 | 6:26 | 220260292 | 7100296583 | 1 | AMC | ENOC | 1069 | DXB | Walk-in Chiller high temperature | BIJU | SANOJ/KADER | 14:30 | 16:30 | FOUND LOW GAS /AFTER GAS CHARGE NOW WORKING NORMAL | USED:- 404 A - 1NOS |  | COMPLETED | WORK COMPLETED
2026-02-10 | 9:44 | 220260293 | 220260293 | 1 | AMC | TCS | ROVE DOWNTOWN | DXB | BAKERY CHILLER HIGH TEMP. | MOHAMMED |  | 14:45 | 15:30 | FOUND LOW GAS /AFTER GAS CHARGE NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 10:26 | 220260294 | 220260294 | 1 | AMC | NESTO | AJE | AJM | FREEZER ROOM LIGHT NOT WORKING | RACEL | ROGER | 17:05 | 20:20 | FOUD 4 LED LIGHT BUSTED /AFTER REPLACE WORKING NORMAL | USED:- LED LIGHT 4 FEET - 4 NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-02-10 | 0:26 | 220260295 | 220260295 | 1 | AMC | BAQER MOHEBI | SATWA | DXB | LIGHTS NOT WORKING | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-10 | 9:26 | 220260296 | 220260296 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | LEAF CHILLER NOT WORKING | SADAM | ZALAUDIN | 20:30 | 21:30 | FOUND CONDENSOR FAN MOTOR STUCK /AFTER CHANGE MOTOR NOW WORKING NORMAL | USED:- 16 W FAN MOTOR - 1 NOS BY TD |  | COMPLETED | WORK COMPLETED
2026-02-10 | 10:47 | 220260297 | 220260297 | 1 | AMC | AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | VEGETABLE FREEZER NOT WORKING | VIGNESH | SELVAN | 16:00 | 19:30 | FOUND LEAK FROM HP LINE REQUESTED TO MATIREAL | NEED:- HP HOSE, GAS HP, JUNTION HOSE | NEED RESCHEDULE | ATTENDED | NEED MATERIAL
2026-02-10 | 10:54 | 220260298 | 220260298 | 1 | AMC | NESTO | AL MINA | DXB | DELI SECTION WATER LEAKAG | MOHAMMED |  | 18:00 | 18:50 | FOUND THE DRAIN LINE BLOCK /AFTER CLEAR NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 11:04 | 220260299 | 220260299 | 1 | AMC | NESTO | AL AIN | AL AIN | CHILLER TEMP ISSUE. | TALIB |  | 16:50 | 19:30 | FOUND THE CHILLER WORKING NORMAL /JUST SET THE SETTING POINT |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 11:58 | 220260300 | 220260300 | 1 | AMC | NESTO | AJG | AJM | FREEZER NO .6 TEMP ISSUE | RACEL | ROGER | 16:43 | 19:04 | FOUND ICE FORMATION IN EVAPORATER AFTER CLEAN ALL ICE NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 9:00 | 220260301 | 220260284 | 2 | AMC | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | WATER LEAKAGE | AHSAN |  | 20:40 | 21:30 | FOUND THE WATER PUMP NOT FIXED NEED TO FIX WATER PUMP | NEED:- VALVE CONDENSSOR PUMP - 1NOS,CLEAR PVC PIPE - 4 MTR |  | ATTENDED | NEED MATERIAL
2026-02-10 | 9:00 | 220260302 | 7100296281 | 2 | AMC | ENOC | 1057 | DXB | walk in chiller temp is breakdown | MOHAMMED |  | 10:40 | 12:30 | FOUND ICE FORMATION /AFTER REMOVE ICE UNIT WORKING NOW NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 9:00 | 220260303 | 220260260 | 2 | AMC | NESTO | AJE | AJM | ICE MACHINE DAMAGE | RACEL | ROGER | 9:10 | 20:20 | FOUND THE OLD ICE MAKER WATER PUMP FROM STORE AND FIXED NOW BUT NEED NEW WATER PUMB | NEED:- WATER PUMP |  | ATTENDED | NEED MATERIAL
2026-02-10 | 9:00 | 220260304 | 7100296296 | 2 | AMC | ENOC | 1099 | DXB | C-store Chiller Display Shelves Repaint | BIJU | SANOJ/KADER | 10:15 | 14:00 | CHECKED THE CHILLER SHELVES AND BAR ARMS .NEED TO BE REPAINTING | NEED TOBE REPAINTING |  | ATTENDED | NEED MATERIAL
2026-02-10 | 16:07 | 220260305 | 220260305 | 1 | AMC | NESTO | AJJ | AJM | FREEZER TEMP.ISSUE | RACEL | ROGER | 20:52 | 21:30 | FOUND THE SOLENOID COIL DAMAGE AFTER CHANGING NOW WORKING NORMAL | USED :- SOLENOID COIL AND DANFOSS SOCKET BY TD |  | COMPLETED | WORK COMPLETED
2026-02-10 | 8:00 | 220260306 | 220260306 | 1 | AMC | AD COOP/DEYAAR | AL MINA | AUH | BURNING SMELL FROM FREEZER B51 | TROVEE/RANDOLPH | ALLAN | 8:20 | 12:00 | FOUND BURNING SMELL FROM HEAD OF THE CABINET WIREING BOX BURN /AFTER CLEAR THE WIRING NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 8:00 | 220260307 | 220260307 | 1 | AMC | AD COOP/DEYAAR | AL MINA | AUH | PLUG IN FREEZER TRIPPING ISSUE. | TROVEE/RANDOLPH | ALLAN | 8:20 | 12:00 | FOUND WIRING BOX HAS WATER /AFTER DRY SWITCH ON NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 16:25 | 220260308 | 220260308 | 1 | AMC | CAREEM | AL SAFA | DXB | CHECK DOOR GASKET | SHABEEB |  | 22:00 | 22:45 | FOUND THE GASKET REMOVED FROM SLOT AFTER FIXING WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 8:00 | 220260309 | 220260309 | 2 | AMC | TCS | ROVE DOWNTOWN | DXB | FREEZER CABINET TEMP.ISSUE | MOHAMMED |  | 13:30 | 14:40 | FOUND COMPRESSORE HAS DAMAGE | NEED:- NT2170U COMPRESSORE AND INSTATATION ITEMS |  | ATTENDED | NEED MATERIAL
2026-02-10 | 16:54 | 220260310 | 220260310 | 1 | AMC | TCS | UMS | DXB | PLUG IN CHILLER NOT WORKING | SHABEEB |  | 20:30 | 21:30 | FOUND THE PLUG LOSS CONNECTION AFTER CONNECTING NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 8:00 | 220260311 | 220260311 | 1 | AMC | LINDE HELIUM | JABAL ALI PORT | DXB | GAS CHARGING | AHSAN | SARAVANAN | 12:40 | 16:00 | CHARGED GAS NOW UNITS ARE WORKING NORMAL | USED:- 407 -3 CYLD |  | COMPLETED | WORK COMPLETED
2026-02-10 | 17:28 | 220260312 | 220260312 | 1 | AMC | TCS | UMS | DXB | BACKERY SECTION TEMP. ISSUE | SHABEEB |  | 20:30 | 21:30 | FOUND AIR FLOW IN UNIT HAS BLOCKED WITH ITEMS AFTER REMOVE WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 17:02 | 220260313 | 220260313 | 2 | AMC | NESTO | AJC | DXB | WATER LEAKAGE | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-10 | 10:00 | 220260314 | 220260314 | 1 | AMC | LULU | AL WATHBA | AUH | MILK CHILLER SMELL BAD | FROILAN | OLIVER/WILLOM | 11:58 | 13:04 | FOUND DRAIN BLOCK IN CABINET AFTER VACCUM AND CLEAN NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 10:00 | 220260315 | 220260315 | 1 | AMC | WESTLAND | AL AIN | AL AIN | GLASS CHILLER CONDENSOR LEAK | TALIB |  | 10:30 | 15:10 | FOUND LEAK AFTER LEAK ARREST NOW SYSTEM WORKING NORMAL | USED:- R22 - NOS BY STORE |  | COMPLETED | WORK COMPLETED
2026-02-10 | 18:33 | 220260316 | 220260316 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | WATER LEAKAGE FROM MONOBLOCK | FROILAN | OLIVER | 8:50 | 9:50 | FOUND DRAINBLOCK AFTER DRAIN CLEAN NOW NORMAL WORKING |  |  | ATTENDED | ATTEND ON 11/2/2026
2026-02-10 | 8:52 | 220260317 | 220260317 | 2 | AMC | NESTO | AJE | AJM | DELI SECTION TEMP ISSUE | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-10 | 8:00 | 220260318 |  | 0 | AMC | AMAZON | AUH | AUH | PPM | KALAMUDIN | SAIF |  |  | PPM DONE Q 1 |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 8:00 | 220260319 | 7100296257 | 3 | AMC | ENOC | 4014 | DXB | water leaking in the chiller | SARVANAN |  | 19:30 | 7:40 | FOUND DRAIN LINE BLOCK /AFTER CLEAN NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 8:00 | 220260320 |  | 0 | AMC | ENOC | 1069 | DXB | PPM | BIJU | SHANOJ/KADER |  |  | PPM DONE Q 4 |  |  | COMPLETED | WORK COMPLETED
2026-02-10 | 8:00 | 220260321 |  | 0 | AMC | ENOC | 1099 | DXB | PPM | BIJU | SHANOJ/KADER |  |  | PPM DONE Q 4 |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 8:00 | 220260322 | 220260313 | 2 | AMC | NESTO | AJC | DXB | WATER LEAKAGE | VIGNESH | SELVAN | 10:30 | 12:00 | FOUND DRAIN BLOCK AFTER DRAIN CLEAN NOW SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 8:00 | 220260323 | 220260316 | 2 | AMC | AD COOP/DEYAAR | AWQAF | AUH | WATER LEAKAGE FROM MONOBLOCK | FROILAN | OLIVER/WILLOM | 11:58 | 13:04 | FOUND DRAIN BLOCK IN CABINET AFTER VACCUM AND CLEAN NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 8:00 | 220260324 | 220260317 | 2 | AMC | NESTO | AJE | AJM | DELI SECTION TEMP ISSUE | RACEL |  | 9:57 | 12:45 | FOUND EVAPORATOR NOT IN GOOD CONDITION ALSO LESS GAS /AFTER CHARGE GAS SYSTEM NOW NORMAL TEMPERATURE | NEED:- REPLACE EVAPORATOR |  | COMPLETED | WORK COMPLETED
2026-02-11 | 9:00 | 220260325 | 220260325 | 1 | AMC | NESTO | AJG | AJM | CHILLER BACK STORE AND DISPLAY CHILLER LIGHT NOT WORKING | RACEL | ROGER | 14:11 | 16:10 | FOUND LIGHT IS BUSTED AFTER REPLACE NOW WORKING NORMAL | USED: 2PSC FLOURESCENT TUBE |  | COMPLETED | WORK COMPLETED
2026-02-11 | 7:09 | 220260326 | 220260326 | 1 | AMC | ASWAQ | GHALILAH | RAK | FROZEN FREEZER NOT WORKING | AHSAN |  | 10:30 | 13:15 | CHECKED THE UNIT FOUND THE ONE EVAPORATOR NOT WORKING AND FOUND LEAK IN VIBRATION ELIMINATOR | NEED: 1 1/8 VIBRATION ELEMINATOR, GAS R22 AND INSTALLATION MATERIAL |  | ATTENDED | NEED MATERIAL
2026-02-11 | 7:09 | 220260327 | 220260079 | 4 | AMC | GRANDIOSE | SOUQ AL BAHAR | DXB | NEED TO CHECK COMPRESSOR | SADAM | ZALAUDIN | 0:30 | 4:00 | REPLACED THE COMPRESSOR NOW WORKING NORMAL | USED :- COMPRESSOR AND INSTALAION ITEMS |  | COMPLETED | WORK COMPLETED
2026-02-11 | 10:00 | 220260328 | 220260328 | 1 | AMC | BANIYAS COOP | SARAB | DXB | CHEESE SECTION CHILLER NOT WORKING | FROILAN | OLIVER | 10:59 | 11:27 | FOUND LOW GAS /AFTER GAS CHARGE NOW WORKING NORMAL | USED: R290 BY STORE |  | COMPLETED | WORK COMPLETED
2026-02-11 | 10:00 | 220260329 | 220260329 | 1 | AMC | ANSAR | KARAMA | DXB | BACK STORE ROOM WATER LEAKAGE | SARAVANAN |  | 12:30 | 13:00 | FOUND DRAIN LINE BLOCK /AFTER CLEAN NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 10:00 | 220260330 | 220260330 | 1 | AMC | NESTO | FUJEIRAH | FUJ | SALAD SECTION TEMP ISSUE | VIGNESH | SELVAN | 14:30 | 15:40 | CHECKED THE DIGITAL CONTROLLER FOUND SETTING IS DIFFERENT AFTER CHENGE SETTING NOW SYSTEM WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 8:00 | 220260331 | 220260331 | 1 | AMC | NESTO | AL FAHIDI | DXB | BUTCHERY CHILLER TCE FORMATION | SHABEEB |  | 1:00 | 1:43 | FOUND DRAIN WATER STOCK IN TRAY AFTER REMOVE ICE FORMATION AND CLEAN DRAIN NOW SYSTEM WORKING NORMAL NEED DRAIN HEATER | NEED:- FLEXIBLE DRAIN HEATER - 3.5 MTR - 2 NOS |  | ATTENDED | NEED MATERIAL | WORK ATTEND ON 10/2/2026
2026-02-11 | 9:47 | 220260332 | 7100296909 | 2 | AMC | ENOC | 412 |  | OPEN CHILLER WATER LEAKAG | AHSAN |  | 18:25 | 20:05 | FOUND CONTROLLER DAMGE NEED TO REPLACE DIGITAL CONTROLLER | NEED:- DIGITAL CONTROLLER ,CONDUCTOR |  | ATTENDED | NEED MATERIAL
2026-02-11 | 10:49 | 220260333 |  | 0 | AMC | ENOC | 95 |  | OPEN CHILLER WATER LEAKAG NO.4 | SADAM | ZALAUDIN | 20:00 | 21:55 | FOUND DRAIN BLOCK/AFTER DRAIN CLEAN NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 10:49 | 220260334 | 220260334 | 1 | AMC | AMAZON |  | AUH | PPM | KALAMUDIN | SAIF/ANWER |  |  | PPM DONE Q 4 |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 12:20 | 220260335 | 220260335 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | FISHERY SECTION CHILLER LEAKAGE | TROVEE/RANDOLPH |  | 11:10 | 12:15 | FOUND DRAIN HEATER DAMAGE NEED TO REPLACE | NEED:- DRAIN HEATER - 230 V - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-11 | 12:00 | 220260336 | 7100296759 | 1 | AMC | ENOC | 1008 |  | display chiller, temperature is high | SADAM | ZALAUDIN | 19:00 | 19:15 | CHILLER NOT OUR SCOOP |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 12:00 | 220260337 | 7100296766 | 1 | AMC | ENOC | 1074 |  | Condenser Cleaning/Refrigeration PM | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-11 | 12:00 | 220260338 | 7100296826 | 2 | AMC | ENOC | 1032 |  | Walk in freezer ice formation | [7 empty] | NOT ATTENDED | RESCHEDULE
2026-02-11 | 12:00 | 220260339 | 7100296839 | 1 | AMC | ENOC | 1043 |  | WALK IN FREEZER ICE FORMATION | SARAVANAN |  |  | 18:22 | NEED TO REPLACE GASKET | NEED:- GASKET |  | ATTENDED | NEED MATERIAL
2026-02-11 | 12:00 | 220260340 |  | 0 | AMC | ENOC | 4037 |  | EQUITY WATER LEAK | SABITH ALI | ABHIJITH/SUDHEESH | 20:10 | 21:15 | FOUND DRAIN PIPE IS BLOCKED AFTER CLEAN DRAIN NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 15:42 | 220260341 | 220260341 | 1 | AMC | AD COOP/DEYAAR | AL MINA | AUH | UNIT NO.B29 DOOR NOT CLOSING PROPERLY | RANDOLPH | TROVEE | 16:35 | 17:00 | FOUND ICE FORMATION IN RETUN CABLE AFTER REMOVE ICE DORRS ARE WORKING NORMAL | NEED:- FOAM TAP 2 ROLL |  | COMPLETED | WORK COMPLETED
2026-02-11 | 16:00 | 220260342 | 220260342 | 1 | AMC | GOURMET | 1004 AL REEM | AUH | ICE CREAM FREEZER NOT WORKING | OLIVER | FROILAN | 16:25 | 17:20 | FOUND THE CONDENSER FAN STUCK AFTER CLEANING FAN MOTOR NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 16:45 | 220260343 | 220260343 | 1 | AMC | LULU | OLIVE TOWER | AUH | WATER LEAKAGE | RANDOLPH | TROVEE | 17:34 | 18:02 | FOUND DRAIN PAN IS FULL AFTER VACCUM NOW UNIT IS WORKING NOWMAL NO WATER LEAKAGE |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 12:40 | 220260344 | 220260344 | 3 | AMC | BAQER MOHEBI | WAREHOUSE | DXB | NEED TO CHECK ALARM SYSTEM CH NO 6 | MOHAMMED |  | 15:00 | 17:45 | FOUNT LIGHT NOT WORKING NEED GRRN LIGHT UNIT IS WORKING NORMAL | NEED:- GRREN LIGHT |  | ATTENDED | NEED MATERIAL
2026-02-11 | 9:39 | 220260345 | 220260345 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | BAKERY CHILLRE NOT COOLING | MOHAMMED |  | 11:00 | 13:30 | FOUND FAN EVAPORATORE FAN MOTOR DAMAGE AFTER CHANGE WORKING NORMAL | USED:- COOLING FAN 92 X 92 - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-02-11 | 12:40 | 220260346 | 220260346 | 1 | AMC | ASWAQ | AL DHAITH | RAK | DELI COUNTER CH 03 TEMP ISSUE / BUTCHERY COUNTER CHILLER SH 37 TEMP ISSUE | AHSAN |  | 14:50 | 18:00 | FOUND ICE FORMATION IN DELI CHILLER AND LOW GAS IN BUTCHERY CHILLER /AFTER REQTIFIYE COMPLEINT UNIT ARE WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 12:40 | 220260347 | 220260344 | 3 | AMC | BAQER MOHEBI | WAREHOUSE | DXB | NEED TO CHECK ALARM SYSTEM CH NO 3 | MOHAMMED |  | 15:00 | 17:45 | FOUND THE LOW GAS AFTER GAS CHARGE WORKING NORMAL | USED:- R 22 a FROM STORE |  | COMPLETED | WORK COMPLETED
2026-02-11 | 12:40 | 220260348 | 220260344 | 3 | AMC | BAQER MOHEBI | WAREHOUSE | DXB | NEED TO CHECK ALARM SYSTEM CH NO 5 | MOHAMMED |  | 15:00 | 17:45 | FOUND THE COMPRESSOR MACHANICAL FAILURE | NEED TO CHANGE COMPRESSOR ALREADY QOUTED TO COUSTEMER |  | ATTENDED | NEED MATERIAL
2026-02-11 | 1:25 | 220260349 | 220260349 | 1 | AMC | CAREEM | MARINA | DXB | OPEN CHILLER SHUT DOWN | SABITH ALI |  | 2:50 | 3:30 | FOUND PLUG FOR POWER IS BURN NEED TO REPLACE / NOW TEMPRORELY CONNECTED UNIT WORKING NO | NEED:- 3 PIN SOCKET ,3 PIN PLUG |  | ATTENDED | NEED MATERIAL
2026-02-11 | 9:00 | 220260350 | 220260093 | 3 | AMC | ANSAR | KARAMA | DXB | ICE CREEM FREEZER SHUTDOWN | SABITH ALI | ABHIJITH/SUDHEESH | 22:35 | 0:15 | FOUND ELCB TRIPED AFTER TURN ON NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 16:00 | 220260351 | 5000217631 | 2 | AMC | ENOC | 1142 | SHJ | FREEZER COLD ROOM WATER LEAK | RACEL | ROGER | 17:58 | 0:31 | REPLACE DRAIN HEATER AND DRAIN PIPE | USED: DRAINHEATER AND DRAIN FITTINGS |  | COMPLETED | WORK COMPLETED
2026-02-11 | 13:26 | 220260352 |  | 0 | AMC | ENOC | 1069 | DXB | FREEZER SHUT DOUN | SARAVANAN |  | 14:45 | 16:30 | FOUND CONTACTOR HAS DAMAGE AFTER REPLACE NOW WORKING NORMAL | USED:- 32 AMPS CONTACTOR - 1 NOS |  | COMPLETED | WORK COMPLETED
2026-02-11 | 17:34 | 220260353 | 7100297132 | 2 | AMC | ENOC | 1031 | DXB | CHILLER WATER LEAK | SARAVANAN |  | 18:30 | 18:45 | FOUND DRAIN PIPE NOT FIX PROPERLY AFERT FIX NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 20:00 | 220260354 |  | 0 | AMC | ENOC | 1036 | DXB | WALK IN FREEZER TEMP.ISSUE | SADAM | ZALAUDIN | 22:10 | 23:15 | FOUND LOW GAS AND OIL /AFTER CHARGE GAS UNIT WORKING NORMAL BUT NEE TO FILL OIL | NEED:- SL 32 OIL - 1 GALLON USED:- R 404a - 1 NOS BY TD |  | ATTENDED | NEED MATERIAL
2026-02-11 | 20:00 | 220260355 | 220260355 | 1 | AMC | CAREEM | AL QUOZ | DXB | PPM | ABHIJITH | SUDHEESH | 0:40 | 2:30 | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 20:00 | 220260356 | 220260356 | 1 | AMC | AMAZON | AUH 1 | AUH | FCU FAULT | ANWER | IRFAN |  |  | AFTER REPLACE THERMOSTAT NOW WORKING NORMAL |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 8:00 | 220260357 |  | 1 | AMC | ENOC | 2020 | DXB | PPM | MUTHUKUMAR | SANOJ |  |  | PPM DON Q 4 |  |  | COMPLETED | WORK COMPLETED
2026-02-11 | 8:00 | 220260358 |  | 1 | AMC | ENOC | 1062 | DXB | PPM | BIJU | KADER |  |  | PPM DON Q 4 |  |  | COMPLETED | WORK COMPLETED
2026-02-12 | 9:00 | 220260359 | 7100296826 | 2 | AMC | ENOC | 1032 | DXB | Walk in freezer ice formation | SARVANAN |  | 10:00 | 11:45 | FOUND ICE FORMATION IN DOOR PIPE ROLL DRAIN NOT WORKING PROPERLY /UNIT NEED TO SHUT DOWN TO CLEAR ISSUE | NEED :- DOOR GASKET - 6 MTR |  | ATTENDED | NEED MATERIAL
2026-02-12 | 9:18 | 220260360 |  | 0 | AMC | ENOC | 412 | RAK | FREERER HIGH TEMP. AND CHILLER WATER LEAK | RACEL |  | 13:57 | 18:25 | FOUND CONDUNSSOR BLOCK AFTER CLEAN NOW WORKING NORMAL |  |  | COMPLETED
2026-02-12 | 9:35 | 220260361 |  | 0 | AMC | ENOC | 1039 | DXB | ICE FORMATION IN VERTICLE FREEZER | SARVANAN |  | 12:45 | 13:30 | FOUND ICE FORMATION IN THE SIDE OF EVAPORATOR AFTER REMVE ICE AND CHANGING PVC CURTTEN NOW WORKING NORMAL |  |  | COMPLETED
2026-02-12 | 7:45 | 220260362 | 220260362 | 2 | AMC | BANIYAS COOP | SARAB | AUH | FREEZER HIGHT TEMP. | RANDOLPH | TROVEE | 9:24 | 11:10 | FOUND THERE IS A LOW GAS NEED GAS CHARGE AND NEED TO REPLACE DAMAGED SENSORS | NEED:- SUBCOOLER ,GAS,,SENSORE, BLUE ROD |  | ATTENDED | NEED MATERIAL
2026-02-12 | 8:10 | 220260363 | 220260093 | 3 | AMC | ANSAR | KARAMA | DXB | COMBI FREEZER TEMP ISSUE | SHABEEB | MUSTAFA | 22:35 | 24:15 | FOUND ELCB TRIPED AFTER TURN ON NOW WORKING NORMAL | NEED: ELCB |  | ATTENDED | NEED MATERIAL | NO CALL OUT REPORT
2026-02-12 | 9:10 | 220260364 | 220260364 | 1 | AMC | LULU | DIP | DXB | FREEZER TRIP ISSUE | MOHAMMED |  | 9:30 | 11:45 | FOUND FREEZER CABINET HAS TRIPPED AFTER TRUN ON WORKING NORMAL | NEED:- JBG2 LIGHT -4 NOS 24V,DEFROST HEATER - 1 NOS |  | ATTENDED | NEED MATERIAL
2026-02-12 | 8:54 | 220260365 | 220260365 | 1 | AMC | NESTO | AL FAHIDI | DXB | VEG CHILLER WATER LEAK | SABITH ALI | ABHJITH | 23:40 | 2:18 | FOUND THE EMERSON CONTROLLER HAS DAMAGE NEED TO REPLACE /TEMPRORLY UNIT EMERGENCY ON | NEED:- EMERSON CONTROLER |  | ATTENDED | NEED MATERIAL
2026-02-12 | 8:34 | 220260366 | 220260366 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | CHEESE CHILLER TEMP ISSUE. | FROILAN | OLIVER | 15:48 | 17:45 | FOUND CONDENSSOR BLOCKED /AFTER CLEAN CONDENSSOR WORKING NORMAL |  |  | COMPLETED
2026-02-12 | 8:44 | 220260367 | 220260367 | 1 | AMC | AD COOP/DEYAAR | AWQAF | AUH | BUTCHERY CHILLER STORE ROOM IS NOT COOLING | FROILAN | OLIVER | 10:05 | 11:21 | FOUND LOW GAS IN SYSTEM /AFTER CHARGE GAS NOW WORKING NORMAL | USED:- R 404a BY BRANCH |  | COMPLETED
2026-02-12 | 10:47 | 220260368 | 220260368 | 1 | AMC | EVERMORE | DIP | DXB | WATER LEAKAGE | MOHAMMED | DENIIS | 13:30 | 14:50 | FOUND DRAIN BLOCK IN LINE AFTER REMOVE BLOCK AND CLEAR DRAIN NOW OK |  |  | COMPLETED
2026-02-12 | 9:00 | 220260369 | 7100296909 | 2 | AMC | ENOC | 412 | RAK | OPEN CHILLER WATER LEAKAG/CHENGEING CONTROLER | RACEL | ROGER | 13:57 | 18:27 | REPLACED THE CONTROLLER WITH SENSOR | USED:- CONTROLLER AND SENSORE |  | COMPLETED
2026-02-12 | 11:30 | 220260370 | 7100296976 | 1 | AMC | ENOC | 1022 | DXB | Ice formation inside freezer | [7 empty] | NOT ATTENDED
2026-02-12 | 11:30 | 220260371 | 7100296983 | 1 | AMC | ENOC | 1036 | DXB | Walk-in chiller gasket and door rubber | [7 empty] | NOT ATTENDED
2026-02-12 | 11:30 | 220260372 | 7100296984 | 1 | AMC | ENOC | 1042 | DXB | pronto chillier door | MUSTAFA |  | 17:45 | 18:00 | FOUND UNIT NOT IN OUR SCOOP |  |  | COMPLETED | NOT OUR SCOPE
2026-02-12 | 11:30 | 220260373 | 7100296996 | 1 | AMC | ENOC | 6568 |  | Door Freezer |  |  |  |  | FOUND UNIT NOT IN OUR SCOOP |  |  | COMPLETED | NOT OUR SCOPE
2026-02-12 | 11:30 | 220260374 | 7100296998 | 1 | AMC | ENOC | 32 |  | Open chiller in CStore 2 water leaking | [7 empty] | NOT ATTENDED
2026-02-12 | 11:30 | 220260375 | 7100297008 | 1 | AMC | ENOC | 1444 | RAK | Water droppings walk-in chiller ceiling. | RACEL | ROGER | 19:05 | 19:00 | FOUND RUST IN EVAPORATOR COVER AFTER CLEAR RUST AN CLEAR WATER DROPPING ISSUE NOW OK |  |  | COMPLETED
2026-02-12 | 11:30 | 220260376 | 220260376 | 1 | AMC | NESTO | MAYSALOON | SHJ | PPM ALL CHILLER CABINETS AND FREEZER CABINETS | VIGNESH |  | 11:15 | 12:30 | PPM DONE |  |  | COMPLETED | WORK COMPLETED
2026-02-12 | 11:30 | 220260377 | 220260377 | 2 | AMC | CAREEM | AL RAFFA | DXB | CHILLER DOOR FRAME BROKEN | [7 empty] | ATTENDED | ON 13/2/2026
2026-02-12 | 12:25 | 220260378 | 220260378 | 1 | AMC | BAQER MOHEBI | AL NAHDA | DXB | F& V CHILLER NOT WORKING | VIGNESH |  | 13:40 | 14:40 | FOUND CONDENSSOR FAN DAMAGED NEED TO REPLACE | NEED:- AXIAN FAN MOTOR |  | ATTENDED | NEED MATERIAL
2026-02-12 | 11:00 | 220260379 | 220260379 | 1 | AMC | NESTO | FUJEIRAH | FUJ | DELI CHILLER TRMP ISSUE | AHSAN |  | 15:30 | 17:40 | FOUND THE WATER LEAKAGE AND BRAKER TRIPPING ISSUE / AFTER CLEAR NOW WORKING NORMAL |  |  | COMPLETED
2026-02-12 | 10:00 | 220260380 | 220260380 | 1 | AMC | AD COOP/DEYAAR | DANA | AUH | LIGHT NOT WORKING IN FREEZER | FROILAN | OLIVER | 11:43 | 12:09 | FOUND THE LIGHT WIRE HAS BROKEN NEED TO REPLACE | NEED:- LED LIGHT AND DRIVE |  | ATTENDED | NEED MATERIAL
2026-02-12 | 10:00 | 220260381 | 220260381 | 1 | AMC | AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | WATER LEAKAGE FROM F&V CHILLER | FROILAN | OLIVER | 12:31 | 13:09 | FOUND WATER FLOW DUE TO DRAINAGE IS BLOCKED AFTER CLEAN DRAIN NOW WORKING NORMAL |  |  | COMPLETED
2026-02-12 | 11:45 | 220260382 | 220260382 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | DOOR IS CLOSING PROPERLY ICE CREAM FREEZER | RANDOLPH | TROVEE | 11:39 | 11:50 | FOUND DOOR GASKET HAS DAMAGE NEED TO BE REPLACE | NEED:- DOOR GASKET - 50 MTR(WITH MAGNET) |  | ATTENDED | NEED MATERIAL
2026-02-12 | 11:45 | 220260383 | 220260383 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | F & V CHILLER NOT WORKING | RANDOLPH | TROVEE | 11:39 | 11:50 | FOUND ICE FORMATION IND THE UNIT AFTER REMOVE ICE AND CONTACTOR CLEAN NOW SYSTEM WORKING NORMAL |  |  | COMPLETED
2026-02-12 | 11:45 | 220260384 | 220260384 | 1 | AMC | AD COOP/DEYAAR | SHAMKHA | AUH | BUTCHERY SECTION FREEZER NOT WORKING | RANDOLPH | TROVEE | 11:39 | 12:37 | FOUND ICE FORMATION IND THE UNIT AFTER REMOVE ICE AND CONTACTOR CLEAN NOW SYSTEM WORKING NORMAL |  |  | COMPLETED
2026-02-12 | 2:00 | 220260385 | 220260385 | 1 | AMC | NESTO | WAREHOUSE | DXB | F & V CHILLER NOT WORKING | SADAM |  | 19:20 | 21:00 | FOUND DOOR NOT CLOSING PROPERLY NEED TO CHANGE | NEED:- DOOR LOCK |  | ATTENDED | NEED MATERIAL
2026-02-12 | 3:08 | 220260386 | 220260386 | 2 | AMC | NESTO | AJE | AJM | BUTCHERY COLD ROOM MONOBLOCK WATER LEAKING | AHSAN | [6 empty] | ATTENDED | ON 13/2/2026
2026-02-12 | 2:53 | 220260387 | 220260387 | 1 | AMC | AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER NO 7 TEMP ISSUE | RANDOLPH | TROVEE | 16:24 | 17:20 | FOUND THE FAN MOTOR STUCK NEED TO BE REPLACE | NEED:- FAN MOTOR 10-20 - 1 NOS WITH GURD AND BLADE |  | ATTENDED | NEED MATERIAL
2026-02-12 | 2:58 | 220260388 | 220260388 | 1 | AMC | AD COOP/DEYAAR | MADINAT ZAYED | AUH | CHILLER WATER LEAKAGE | RANDOLPH | OLIVER/TROVEE/FROILAN | 18:15 | 18:35 | FOUND DRAIN PIPE HOSE DAMAGE NEED TO REPLACE | NEED:- DRAIN HOSE |  | ATTENDED | NEED MATERIAL
2026-02-12 | 16:05 | 220260389 | 220260389 | 1 | AMC | AD COOP/DEYAAR | AL MINA | AUH | B 35 FREEZER TEMP. ISSUE ITEMS ARE MELTING | RANDOLPH | OLIVER/TROVEE/FROILAN | 19:10 | 20:35 | FOUND DEFROST HEATER IS DEFECTED | NEED:- DEFROST HEATER 375 CM 230V |  | ATTENDED | NEED MATERIAL
2026-02-12 | 17:08 | 220260390 | 220260390 | 1 | AMC | LULU | AL KHAIR | AL AIN | FREEZER WATER LEAKAGE | TALIB |  | 18:10 | 18:45 | FOUND THE DRAIN PIPE NOT FIXED PROPER AFTER FIXING NOW OK |  |  | COMPLETED
2026-02-12 | 13:00 | 220260391 | 220260391 | 1 | AMC | GRANDIOSE | HOOR 17 | DXB | FREEZER TEMP ISSUE. | SHABEEB | MUSTAFA | 14:50 | 15:10 | FOUND THE UNIT IS WORKING NORMAL GRANDIOSE PEPOLE ALREDY CLEAR ICE FORMATION |  |  | COMPLETED
2026-02-12 | 19:00 | 220260392 | 220260392 | 1 | AMC | ASWAQ | SOUTH AL DAITH | RAK | CHILLER CABINET HIGH TEMP | RACEL | ROGER | 20:05 | 21:15 | FOUND LESS GAS CHECKED SOME LAEKAGE ISSUE IN UNIT NEED TO CHECK FULL SYSTEM |  |  | ATTENDED | RESCHEDULE
2026-02-12 | 11:45 | 220260393 | 220260393 | 1 | AMC | CAREEM | AL RAHA | AUH | DOOR NOT CLOSING | TROVEE | RANDOLPH | 13:10 | 14:10 | FOUND DOOR OUT OF FRAME DAMAGE ALSO AFTER APPLY SILLICON AND RESET THE DOOR |  |  | COMPLETED
2026-02-12 | 8:00 | 220260394 | 220260282 | 2 | AMC | NESTO | WAREHOUSE | DXB | COLD ROOM DOOR ISSUE | SHABEEB | MUSTAFA | 13:00 | 14:30 | FOUND THE DOOR HANDEL PROBLEM NEED TO REPLACE | USED:- COLD ROOM DOOR HANDEL SET |  | COMPLETED
2026-02-12 | 8:00 | 220260395 | 220260395 | 1 | AMC | HYPERMAX | 360 MALL | KWT | PPM CABINET CLEANING | RAUL |  |  |  | PPM CABINET |  |  | COMPLETED
2026-02-12 | 8:00 | 220260396 |  | 0 | AMC | ENOC | 1056 | DXB | PPM | SANOJ | MUSTAFA |  |  | PPM DONE Q4 |  |  | COMPLETED
2026-02-12 | 8:00 | 220260397 |  | 0 | AMC | ENOC | 1632 | DXB | PPM | BIJU | KADER |  |  | PPM DONE Q4 |  |  | COMPLETED
2026-02-12 | 8:00 | 220260398 | 220260398 | 1 | AMC | HYPERMAX | CITY CENTER | OMR | PPM IN DELI CHILLER | MOHAMMAD SHANTA |  |  |  | PPM DONE |  |  | COMPLETED
2026-02-12 | 8:00 | 220260399 | 220260399 | 1 | AMC | HYPERMAX | SALALAH | OMR | DELI CHILLER WATER LEAKAGE ISSUE | ALISON |  |  |  | FOUND DRAINBLOCK AFTER DRAIN CLEAN NOW NORMAL WORKING |  |  | COMPLETED
2026-02-12 | 8:00 | 220260400 |  | 0 | AMC |  |  |  | DRIVING | WISLON |  | 8:30 | 6:30 | DRIVING |  |  | COMPLETED
2026-02-13 | 8:00 | 220260401 | 220260401 | 1 | AMC | HYPERMAX | SALALAH | OMR | MINUS RANGE COMPRESSOR NO 2 TRIPPING ISSUE | ALISON |  |  |  | FOUND LESS OIL IN COMPRESSOR NEED TO CHARGE OIL | NEED:- OIL CHARGE |  | ATTENDED | NEED MATERIAL
2026-02-13 | 9:00 | 220260402 | 220260386 | 2 | AMC | NESTO | AJE | AJM | BUTCHERY COLD ROOM MONOBLOCK WATER LEAKING | AHSAN |  | 9:40 | 10:45 | CHECKED THE DRAIN TRAY HAS BLOCKED AFTER CLEAN NOW WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 11:47 | 220260403 | 220260403 | 1 | AMC | NESTO | AJJ | AJM | FREEZER TEMP. NORMAL BUT LOW AIR FLOW | AHSAN | SELVAN | 14:00 | 19:00 | FOUND ICE FORMATION AFTER REMOVE ICE WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 6:28 | 220260404 | 220260404 | 1 | AMC | BANIYAS COOP | SHAHAMA | AUH | FREEZER TEMP.ISSUE AND SOUND IN UNIT | FROILAN | TROVEE | 11:35 | 14:40 | FOUND ICE FORMATION AFTER REMOVE ICE RESET UNIT WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 6:28 | 220260405 | 220260362 | 2 | AMC | BANIYAS COOP | SARAB | AUH | FREEZER COLD ROOM NOT WORKING | RANDOLPH | TROVEE/FROILAN | 9:30 | 10:03 | FOUND THAT ROCKER SWITCH IS LOOSE CONTACT,NEED TO CHANGE | NEED:- ROCKER SWITCH - 1PCS |  | ATTENDED | NEED MATERIAL
2026-02-13 | 9:40 | 220260406 | 220260406 | 1 | AMC | BAQER MOHEBI | ABU HAIL | SHJ | FREEZER LIGHT NOT WORKING | AHSAN | SELVAN | 11:40 | 12:20 | FOUND TUBE LIGHTS ARE NOT WORKING, NEED TO CHANGE | NEED:- TUBE LIGHTS |  | ATTENDED | NEED MATERIAL
2026-02-13 | 14:10 | 220260407 | 220260407 | 1 | AMC | CAREEM | MOTOR CITY | DXB | CHILLER WATER LEAK AND DOOR ISSUE | SADAM |  | 20:00 | 21:00 | FOUND DRIN HOSE REMOVED AFTER FIX NOW WORKING AND DOOR NEED TO REPLACE THE SLIDING ROLLER HOLDER SET - 1 | NEED:- SLIDING HOLDER - 1 SET |  | ATTENDED | NEED MATERIAL
2026-02-13 | 14:17 | 220260408 | 220260408 | 1 | AMC | NESTO | AJC | AJM | ICE MACHINE NOT WORKING | AHSAN | SELVAN | 19:55 | 21:00 | FOUND THE ICE MAKER RUBBER ANTI VIBRATION BUSH HAS DAMAGE NEED TO REPLACE | NEED:- RUBBER ANTI VIBRATION BUSH - 1 NOS . | NEED TO SHUT DOWN UNIT | ATTENDED | NEED MATERIAL
2026-02-13 | 6:00 | 220260409 | 220260079 | 4 | AMC | GRANDIOSE | SOUQ AL BAHAR | DXB | NEED TO CHECK COMPRESSOR | SARAVANAN | ZALAUDIN | 7:10 | 7:30 | FOUND IN THE UNIT NO SOUND /THE SOUND IS FROM FCU FAN |  |  | COMPLETED
2026-02-13 | 14:45 | 220260410 | 220260410 | 1 | AMC | AD COOP/DEYAAR | SPAR SAADIAYT | AUH | CHEESE SECTION SHUT DOWN | RANDOLPH | TROVEE | 17:15 | 18:15 | FOUND THE CONTROLLER IS OFF AFTER SWITCH ON WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 14:45 | 220260411 | 220260411 | 1 | AMC | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | FROZEN FREEZER NOT WORKING | SABITH ALI | ABHIJITH | 19:10 | 21:00 | FOUND ICE FORMATION IN EVAPORATOE AFTER REMOVE ICE NOW SYSTEM IS WORKING AND FOUND DRAIN PIPE HAS DAMAGED NEED TO CHANGE | NEED:- FLEXIBLE DRAIN PIPE - 1 MTR |  | ATTENDED | NEED MATERIAL
2026-02-13 | 8:14 | 220260412 | 220260412 | 1 | AMC | AD COOP/DEYAAR | MUROOR | AUH | BUTCHERY COLD ROOM MONOBLOCK ICE FORMATION | FROILAN | OLIVER | 15:22 | 16:30 | FOUND THE ICE FORMATION IN EVAPORATOR AFTER REMOVE ICE WORKING NORMAL (NEED HEATER ROD STRAIGHT) | NEED:-HEATER ROD STRAIGHT-2PCS |  | ATTENDED | NEED MATERIAL
2026-02-13 | 15:03 | 220260413 | 220260413 | 1 | AMC | HOP | JABAL ALI | DXB | FEMALE CHANGING ROOM AC NOT WORKING | [7 empty] | NOT ATTENDED
2026-02-13 | 10:00 | 220260414 | 7100297132 | 2 | AMC | ENOC | 1031 | DXB | chiller pipe is leaking | [7 empty] | COMPLETED | ATTEND ON 11/2/2026
2026-02-13 | 10:00 | 220260415 | 7100297136 | 1 | AMC | ENOC | 1063 | DXB | Pronto display chiller air filter | [7 empty] | NOT ATTENDED
2026-02-13 | 10:00 | 220260416 | 7100297163 | 2 | AMC | ENOC | 1507 | DXB | Walking Chiller temperature abnormal | VIGNESH | [6 empty] | COMPLETED | ATTEND ON 07/2/2026
2026-02-13 | 10:00 | 220260417 | 7100297184 | 1 | AMC | ENOC | 1047 | DXB | walk-in freezer | [7 empty] | NOT ATTENDED
2026-02-13 | 10:00 | 220260418 | 7100297185 | 1 | AMC | ENOC | 1079 | DXB | Deli Counter Chiller light is not working | [7 empty] | NOT ATTENDED
2026-02-13 | 10:00 | 220260419 | 7100297202 | 1 | AMC | ENOC | 1094 | DXB | walk in freezer ice formation in condens | SADAM |  | 21:30 | 23:40 | ICE FORMATION IN EVAPORATORE AFTER RENOVE ICE NOW WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 10:00 | 220260420 | 7100297222 | 1 | AMC | ENOC | 1035 | DXB | Walk in freezer not working | SARVANAN |  | 15:30 | 432:00 | FOUND LOSE CONNECTION IN POWER SOCKET AFTER REPAIR NOW WORKING NORMAL |  |  | COMPLETED | ATTEND ON 12/2/2026
2026-02-13 | 10:00 | 220260421 | 7100297237 | 1 | AMC | ENOC | 2020 | DXB | Pronto walk in freezer | SADAM |  | 18:30 | 19:30 | FOUND CONDENSORE FAN MOTOR HAS NOT WORKING AFTER REPLACE NOW SYSTEM IS WORKING NORMAL | USED:- 16 W FAN MOTOR - 1 NOS BY TD |  | COMPLETED
2026-02-13 | 10:00 | 220260422 | 7100297287 | 1 | AMC | ENOC | 1052 | DXB | open chiller showing high temp 10.1 | MOHAMMED |  | 15:00 | 15:55 | VISIT STORE UNITS ARE WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 8:00 | 220260423 | 220260309 | 2 | AMC | TCS | ROVE DOWNTOWN | DXB | FREEZER CABINET TEMP.ISSUE/CHANGING COMPRESSOR | SARAVANAN | SHABEEB | 9:30 | 15:12 | REPLACED COMPRESSOR NOW WORKING NORMAL | USED:- NT2170U COMPRESSORE AND INSTATATION ITEMS |  | COMPLETED
2026-02-13 | 10:25 | 220260424 | 220260424 | 1 | AMC | TCS | AL AWEER | DXB | CHILLER NO 46 NOT WORKING TRIPPING ISSUE | SARAVANAN | SHABEEB | 15:45 | 16:45 | FOUND TRIPPING ISSUE AFTER SWITCH ON SYSTEM WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 15:25 | 220260425 | 220260425 | 1 | AMC | CAREEM | JVT | DXB | FREEZER COLD ROOM HIGH TEMP | MOHAMMED |  | 16:15 | 18:15 | FOUND COLD ROOM DOOR NOT CLOSE PROPER CLOSE AND SOLENOID GAMAGE AFTER CHANGING WORKING NORMAL | USED:- SOLENOID COIL - 1 NOS BY TD |  | COMPLETED
2026-02-13 | 8:00 | 220260426 | 220260377 | 2 | AMC | CAREEM | AL RAFFA | DXB | CHILLER DOOR FRAME BROKEN | MOHAMMED |  | 12:45 | 14:00 | FOUND DISPLAY CONTROLLER NOT WORKING NEED TO REPLACE | NEED:- CAREL CONTROLLER AND SENSOR |  | ATTENDED | NEED MATERIAL
2026-02-13 | 12:10 | 220260427 |  | 0 | AMC | ENOC | 1204 | DXB | OPEN CHILLER TEMP ISSUE | [7 empty] | NOT ATTENDED
2026-02-13 | 8:00 | 220260428 | 220260175 | 2 | AMC | BANIYAS COOP | SHAHAMA | AUH | CHILLER TEMP ISSUE./EGG CHILLER CHANGING COMPRESSOR | RANDOLPH | OLIVER | 11:35 | 14:40 | REPLACED THE COMPRESSOR NOW WORKING NORMAL | USED :- EMBRACO COMPRESSOR AND INSTALATION MATERIALS |  | COMPLETED | NEED MATERIAL
2026-02-13 | 18:33 | 220260429 |  | 0 | AMC | ENOC | 1036 | DXB | WALK IN FREEZER NOT WORKING | SADAM |  | 24:00 | 6:25 | FOUND SUCTION PIPE CRAKED NEED TO REPLACE | NEED:- 3/4 COPPER PIPE - 1 MTR ,R 404 GAS - 2 NOS,SL 32 - 1 GALLON |  | ATTENDED | NEED MATERIAL
2026-02-13 | 13:00 | 220260430 | 220260430 | 1 | AMC | NESTO | AJJ | AJM | CHILLER NO 1 NOT WORKING | AHSAN | SELVAN | 14:00 | 19:00 | FOUND SOLENOID COIL NOT WORKING AFTER FIXING NOW WORKING NORMAL | USED:- SOLENOID COIL - 1 NOS BY TD |  | COMPLETED
2026-02-13 | 16:00 | 220260431 | 220260431 | 1 | AMC | NESTO | AJJ | AJM | BUTCHERY COUNTER NO 1 EVAPORATOR ICE AND CONTROLLER SHOWING ERROR | AHSAN | SELVAN | 21:25 | 23:45 | FOUND ICE FORMATION IN EVAPORATORE AFTER REMOVE ICE AND RESET CONTROLER SETTING NOW WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 18:45 | 220260432 | 220260432 | 1 | AMC | NESTO | MUWAILHA | SHJ | FREEZER COLD ROOM TEMP.ISSUE | SABITH ALI |  | 4:40 | 6:10 | FOUND ICE FORMATION IN EVAPORATORE AFTER REMOVE ICE AND RESET NOW WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 18:00 | 220260433 | 220260433 | 1 | AMC | PASSONS | FUJEIRAH | FUJ | BUTCHRY SECTION DISPLAY CHILLER TEMP ISSUE | SABITH ALI |  | 0:00 | 3:15 | CHECKED THE AIRFLOW IS BLOCKED WITH ICE FORMATION AFTER REMOVE ICE NOW WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 8:00 | 220260434 | 220260434 | 1 | AMC | CAREEM | DIC | DXB | PPM DONE DUBAI INTERNET CITY STORE | ZALAUDIN | MUSTAFA,JAVEED |  |  | PPM DONE |  |  | COMPLETED
2026-02-13 | 22:00 | 220260435 |  | 0 | AMC | ENOC | 1602 | DXB | VERTICAL FREEZER TEMP ISSUE | [7 empty] | NOT ATTENDED
2026-02-13 | 8:00 | 220260436 |  | 0 | AMC | ENOC | 1079 | DXB | PPM | BIJU | SANOJ |  |  | PPM DONE Q 4 |  |  | COMPLETED
2026-02-13 | 8:00 | 220260437 |  | 0 | AMC | ENOC | 1033 | DXB | PPM | BIJU,MUTHUKUMAR | SANOJ,KADER |  |  | PPM DONE Q 4 |  |  | COMPLETED
2026-02-13 | 20:00 | 220260438 | 220260438 | 1 | AMC | ASWAQ | KHALIFA CITY | RAK | PPM | SUDHEESH | RAMZAN |  |  | PPM DONE |  |  | COMPLETED
2026-02-13 | 20:00 | 220260439 | 220260439 | 1 | AMC | AMAZON | DXB 3 | DXB | PPM DONE Q 1 | ABID | GOVIND,SHAHABUDDIN |  |  | PPM DONE Q1 |  |  | COMPLETED
2026-02-13 | 20:00 | 220260440 | 220260440 | 1 | AMC | HYPERMAX | CITY CENTER | OMR | MEET SECTION CHILLER NOT COOLING | MOHAMMAD SHANTA |  | 15:30 | 19:00 | FOUND CONTROLLER PROBLEM AFTER FIXED NOW WORKING NORMAL |  |  | COMPLETED
2026-02-13 |  | 220260441 | 220260441 | 1 | AMC | LULU | TERRACE MALL | KWT | PLUG IN FREEZER AN AND COLD ROOM BAKERY HIGH TEMP | JOSE LITO |  |  |  | FOUND PLUGIN FREEZER AREA AC NOT WORKING AND COLD ROOM CONDENSSOR CLEAN NOW UNITS ARE WORKING NORMAL |  |  | COMPLETED
2026-02-13 | 8:00 | 220260442 |  | 0 | AMC |  | DRIVING | DXB | DRIVING | WILSON |  | 7:30 | 18:30 | DRIVING - AJMAN, DXB |  |  | COMPLETED
2026-02-14 | 9:22 | 220260443 | 220260443 | 1 | AMC | TCS | ROVE DOWNTOWN | DXB | FREZEER TEMP ISSUE | SARAVANAN | SHABEEB | 11:45 | 12:30 | CHECKED NEED TO REPROSSED /AFTER REPROSSES SYSTEM NOW WPRKING NORMAL | USED:- R 290, 1/4 FILTER DRIER NITROGEN, BLUE ROD |  | COMPLETED
2026-02-14 | 8:14 | 220260444 | 220260444 | 1 | AMC | LULU | AL FORSAN | AUH | FREEZER FAULTY ALARM | RANDOLPH | TROVEE | 9:50 | 11:11 | FOUND LOSE CONNECTION IN POWER SOCKET AFTER REPAIR NOW WORKING NORMAL |  |  | COMPLETED
2026-02-14 | 9:13 | 220260445 | 220260445 | 1 | AMC | LULU | NUAIMIA | SHJ | HOT FOOD CHILLER TEMP ISSUE
2026-02-14 | 10:33 | 220260446 | 220260446 | 1 | AMC | BAQER MOHEBI | BUR DUBAI | DXB | MILK CHILLER HIGH TEMP.
2026-02-14 | 10:33 | 220260447 | 220260447 | 1 | AMC | AD COOP/DEYAAR | SPAR ZAKHER MALL | AL AIN | DISPLAY FREEZER NOT COLLING
2026-02-14 | 11:06 | 220260448 | 220260448 | 1 | AMC | RNQ | AJMAN | AJM | UNIT TRIPPING ISSUE
2026-02-14 | 8:29 | 220260449 | 220260449 | 1 | AMC | NESTO | AJE | AJM | F & V CHILLER TEMP ISSUE
2026-02-14 | 8:32 | 220260450 | 220260450 | 1 | AMC | NESTO | AJG | AJM | COLD ROOM LIGHT NOT WORKING
2026-02-14 | 9:39 | 220260451 | 220260451 | 1 | AMC | NESTO | FUJEIRAH | FUJ | HEAVY NOISE ISSUE
2026-02-14 | 10:06 | 220260452 | 220260452 | 1 | AMC | NESTO | KARAMA | DXB | BAKERY CHILLRE NOT WORKING
2026-02-14 | 10:35 | 220260453 | 220260453 | 1 | AMC | NESTO | AL AIN | AL AIN | FREEZER TEMP ISSUE.
2026-02-14 | 8:00 | 220260454 | 220260454 | 1 | AMC | AD COOP/DEYAAR | BUTEEN | AUH | CHICKEN FREEZER NOT COOLING ITEMS
2026-02-14 | 8:35 | 220260455 | 220260455 | 1 | AMC | AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | COLD ROOM TRIPPING ISSUE
2026-02-14 | 11:02 | 220260456 | 220260456 | 1 | AMC | AD COOP/DEYAAR | MADINAT ZAYED | AUH | CHILLER TRIPPING ISSUE
2026-02-14 | 12:21 | 220260457 | 220260457 | 1 | AMC | ASWAQ | AL DHAITH | RAK | WALKIN FREEZER ISSUE
2026-02-14 | 12:47 | 220260458 | 220260458 | 1 | AMC | NESTO | ARAB MALL | DXB | SALAD CHILLER ICE FORMATION
2026-02-14 | 12:56 | 220260459 | 220260459 | 1 | AMC | NESTO | KARAMA | DXB | FREEZER NOT WORKING
2026-02-14 | 8:00 | 220260460 |  | 0 | AMC | ANSAR | KARAMA | DXB | COMBI FREEZER TEMP ISSUE/ TRIPPINF ISSUE
2026-02-14 | 13:12 | 220260461 | 220260461 | 1 | AMC | BAQER MOHEBI | AL NAHDA | SHJ | FISH CHILLER WATER LEAK
2026-02-14 | 13:32 | 220260462 | 220260462 | 1 | AMC | BANYA FOREST | DUBAI | DXB | CORRIDOOR AC NOT WORKING
2026-02-14 | 18:22 | 220260463 | 220260463 | 1 | AMC | AL AIN COOP | AL MANASIR | AL AIN | FREEZER NO 1 NOT WORKING PROPERLY
2026-02-14 | 20:50 | 220260464 | 220260464 | 1 | AMC | ASWAQ | GHALILAH | RAK | FREEZER AND CHILLER HIGH TEMP.
2026-02-14 | 20:57 | 220260465 | 220260465 | 1 | AMC | PASSONS | FUJEIRAH | FUJ | DELI CHILLER HIGH TEMP.
2026-02-14 | 22:33 | 220260466 | 220260466 | 1 | AMC | CAREEM | AL RAHA | AUH | CHILLER BACK SIDE ICE FORMATION
2026-02-14 | 22:44 | 220260467 | 220260467 | 1 | AMC | HOP | JEBAL ALI | DXB | PENDING TO FIXING LIGHT
2026-02-14 | 11:14 | 220260468 | 220260468 | 1 | AMC | TCS | EMERALD COURT | DXB | PORK SECTION HIGH TEMP.
2026-02-14 | 13:41 | 220260469 | 220260469 | 1 | AMC | NESTO | SATWA | DXB | BUTCHERY CHILLER HIGH TEMP AND BURNING SMELL ISSUE
2026-02-14 | 19:00 | 220260470 | 220260470 | 1 | AMC | NESTO | WAREHOUSE | DXB | F & V CHILLER WATER LEAKAGE
2026-02-14 | 11:00 | 220260471 | 7100297305 | 1 | AMC | ENOC | 4007 |  | chiller water leakage
2026-02-14 | 11:00 | 220260472 | 7100297338 | 1 | AMC | ENOC | 1034 |  | Noisy Display Chiller
2026-02-14 | 11:00 | 220260473 | 7100297341 | 1 | AMC | ENOC | 509 |  | open chiller light holder
2026-02-14 | 11:00 | 220260474 | 7100297345 | 1 | AMC | ENOC | 1035 |  | Deli chiller 1 not working
2026-02-14 | 11:00 | 220260475 | 7100297347 | 1 | AMC | ENOC | 4001 |  | open chiller 2 have water leakage. Kindl
2026-02-14 | 11:00 | 220260476 | 7100297387 | 1 | AMC | ENOC | 1041 |  | Deli counter glass crack
2026-02-14 | 11:00 | 220260477 | 7100297358 | 1 | AMC | ENOC | 1094 |  | freezer temp getting high need to check
2026-02-14 | 11:00 | 220260478 | 7100297353 | 1 | AMC | ENOC | 1081 |  | Chiller, freezer PM service
2026-02-14 | 11:00 | 220260479 | 7100297357 | 1 | AMC | ENOC | 1618 |  | open chiller
2026-02-14 | 11:00 | 220260480 | 7100297343 | 1 | AMC | ENOC | 1204 |  | Open Chiller High Temperature
2026-02-14 | 11:00 | 220260481 | 7100297337 | 1 | AMC | ENOC | 1036 |  | Walkin Freezer temperature
2026-02-14 | 11:00 | 220260482 |  | 0 | AMC | ENOC | 1032 |  | Walkin Freezer temperature issue
2026-02-14 | 8:00 | 220260483 |  | 0 | AMC | ENOC | 1066 |  | PPM
2026-02-14 | 8:00 | 220260484 |  | 0 | AMC | ENOC | 1065 |  | PPM
2026-02-14 |  | 220260485 | 220260485 | 1 | AMC | MONOPRIX | ASSIMAH | KWT | REPLACING FAN MOTORS REPAIRD
2026-02-14 |  | 220260486 | 220260486 | 1 | AMC | LULU | TERRACE MALL | KWT | COLD ROOM FREEZER HIGH TEMP.
2026-02-14 |  | 220260487 | 220260487 | 1 | AMC | HYPERMAX | CITY CENTER | OMR | COLD ROOM AND CABINET PPM
2026-02-14 |  | 220260488 |  | 0 | AMC
2026-02-14 |  | 220260489 |  | 0 | AMC
|  | 220260490 |  | 0 | AMC
91

## ENOC
DATE
2026-02-03
4002 | 5000219010 | 7100295086 | WATER LEAKAGE FROM CHILLER 2
1126 | 6100073651 | 7100295144 | SUPPLY OF COMPRESSOR AND CONSUMABLES
1125 | 6100073652 | 7100295145 | SUPPLY OF COMPRESSOR AND CONSUMABLES
1511 | 5000218991 | 7100295161 | PRONTO VERTICAL FREEZER IS NOT WORKING | 2026-02-04
4037 |  | 7100295232 | CHILLER TEMP.GAUGE | 2026-02-04
1060 |  | 7100295233 | BED FREEZER NOT WORKING | 2026-02-04
DATE
2026-02-05
509 | 6100073800 | 7100295487 | Repainting of shelves with arms and leg | 2026-02-11
1060 | 5000219336 | 7100295593 | bed freezer not working | 2026-02-06 | DONE
1236 | 5000219369 | 7100295676 | door freezer light not working | 2026-02-12 | DONE
2026-02-06
1086 | 5000219471 | 7100295791 | Vertical freezer digital temperature | 2026-02-07 | DONE
1143 | 5000219477 | 7100295795 | Water leakage from Open Chiller | 2026-02-08 | DONE
1203 | 5000219475 | 7100295805 | REACH IN CHILLER noise | 2026-02-07 | NOT OUR SCOPE
4009 | 5000219509 | 7100295931 | Chiller 2 water leaking | 2026-02-07 | DONE
1082 | 5000219539 | 7100295941 | Pronto chiller tubelights not working | 2026-02-13 | DONE
1511 | 6100073864 | 7100295706 | Supply of compressor and consumables for | 2026-02-08 | DONE
DATE
2026-02-07
1022 | 6100073956 | 7100296042 | WALK IN CHILLER DRAIN PIPE LEAKING | Feb 9, 2026 | DONE
1507 | 5000219690 | 7100296061 | Walking chiller temperature abnormal | Feb 8, 2026 | DONE
1074 | 5000219663 | 7100296062 | ICE Formation in Walk in Freezer door | Feb 9, 2026 | DONE
1062 | 5000219676 | 7100296066 | Chiller Door in Pronto Area damaged | Feb 14, 2026
1077 | 5000219601 | 7100296076 | Ice formation in walk in freezer | Feb 8, 2026 | DONE
1142 | 6100073984 | 7100296132 | Supply of condenser fan motor for vertic | Feb 10, 2026 | SUPPLY
1205 | 5000219569 | 7100296055 | Walkin freezer door not closing properly | Feb 14, 2026 | DONE
1079 | 6100073947 | 7100296008 | Supply of door handles for bench chiller | Feb 10, 2026 | DONE
4052 | 6100073952 | 7100296013 | Supply of condenser fan motor for open | Feb 13, 2026 | SUPPLY
DATE
2026-02-09
1143 | 5000219768 | 7100296219 | Open Chiller Drainage blocked | 2026-02-11 | DONE
4014 | 5000219753 | 7100296257 | water leaking in the chiller | 2026-02-10 | DONE
1057 | 5000219750 | 7100296281 | walk in chiller temp is breakdown | 2026-02-10 | DONE
1099 | 5000219731 | 7100296296 | C-store Chiller Display Shelves Repaint | 2026-02-24 | DONE
1013 | 5000219789 | 7100296307 | WALK IN CHILLER TEMPERATURE | 2026-02-10 | DONE
1044 | 5000219846 | 7100296309 | Walking freezer door not closing proper | 2026-02-16 | DONE
1044 | 5000219858 | 7100296388 | Ice forming at walking freezer. | 2026-02-10 | DONE
1205 | 5000219932 | 7100296455 | Walk in Freezer ice formation | 2026-02-11 | DONE
1081 | 5000219857 | 7100296352 | walk in freezer high temperature | 2026-02-10 | DONE
DATE
2026-02-10
1205 | 5000219932 | 7100296455 | Walk in Freezer ice formation | 2026-02-11 | DONE
1074 | 5000219938 | 7100296573 | Walk in freezer door hard to open | 2026-02-17 | DONE
1069 | 5000220016 | 7100296583 | Walk-in Chiller high temperature | 2026-02-11 | DONE
1126 | 5000220024 | 7100296586 | vertical freezer not working | 2026-02-11 | DONE
1125 | 5000220025 | 7100296627 | Walk in freezer not working. | 2026-02-11 | DONE
DATE
2026-02-11
1008 | 5000220116 | 7100296759 | display chiller, temperature is high | 2026-02-11 | DONE
1074 | 5000220081 | 7100296766 | Condenser Cleaning/Refrigeration PM | 2026-02-11 | PPM
1032 | 5000220088 | 7100296826 | Walk in freezer ice formation | 2026-02-11 | DONE
1043 | 5000220211 | 7100296839 | WALK IN FREEZER ICE FORMATION | 2026-02-11 | DONE
412 | 5000220222 | 7100296909 | Cold Drinks Chiller Not Working Properly | 2026-02-11 | DONE
DATE
2026-02-12
1022 | 5000220253 | 7100296976 | Ice formation inside freezer | 2026-02-13 | DONE
1036 | 5000220257 | 7100296983 | Walk-in chiller gasket and door rubber | 2026-02-18
1042 | 5000220235 | 7100296984 | pronto chillier door | 2026-02-18 | DONE
6568 | 5000220259 | 7100296996 | Door Freezer | 2026-02-18 | NOT OUR SCOPE
32 | 5000220278 | 7100296998 | Open chiller in CStore 2 water leaking | 2026-02-12
1444 | 5000220285 | 7100297008 | Water droppings walk-in chiller ceiling. | 2026-02-13 | DONE
DATE
2026-02-13
1031 | 5000220310 | 7100297132 | chiller pipe is leaking | 2026-02-14 | DONE
1063 | 5000220304 | 7100297136 | Pronto display chiller air filter | 2026-02-16
1507 | 5000220412 | 7100297163 | Walking Chiller temperature abnormal | 2026-02-14 | DONE
1047 | 5000220498 | 7100297184 | walk-in freezer | 2026-02-14
1079 | 5000220494 | 7100297185 | Deli Counter Chiller | 2026-02-20
1094 | 5000220543 | 7100297202 | walk in freezer ice formation in condens | 2026-02-15 | DONE
1035 | 5000220443 | 7100297222 | Walk in freezer not working | 2026-02-14 | DONE
2020 | 5000220552 | 7100297237 | Pronto walk in freezer | 2026-02-14 | DONE
1052 | 5000220553 | 7100297287 | open chiller showing high temp 10.1 | 2026-02-14 | DONE
DATE
2026-02-14
4007 | 5000220676 | 7100297305 | chiller water leakage | 2026-02-15
1034 | 5000220614 | 7100297338 | Noisy Display Chiller | 2026-02-15
509 | 5000220668 | 7100297341 | open chiller light holder | 2026-02-21 | DONE
1035 | 5000220598 | 7100297345 | Deli chiller 1 not working | 2026-02-15 | DONE
4001 | 5000220558 | 7100297347 | open chiller 2 have water leakage. Kindl | 2026-02-15
1041 | 5000220580 | 7100297387 | Deli counter glass crack | 2026-02-17
1094 | 5000220639 | 7100297358 | freezer temp getting high need to check | 2026-02-15 | DONE
1081 | 6100074332 | 7100297353 | Chiller, freezer PM service | 2026-02-21 | PPM
1618 | 6100074342 | 7100297357 | open chiller | 2026-02-16 | NOT OUR SCOPE
1204 | 5000220672 | 7100297343 | Open Chiller High Temperature | 2026-02-15 | DONE
1036 | 5000220631 | 7100297337 | Walkin Freezer temperature | 2026-02-15 | DONE

## TABLE DATA
REPEAT COMPLAINTS | (All)
DATE | (All)
CUSTOMER | BRANCH | LOCATION | FAILURE DETAILS | Status | TECH 1 | REPEAT_COMPLAINTS
AD COOP/DEYAAR | ABU DHABI | AUH | FROZEN SECTION WATER LEAKAGE | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | ABU DHABI | AUH | ICE MAKER FISHERY SECTION NOT WORKING | ATTENDED | OLIVER | 2
AD COOP/DEYAAR | ABU DHABI | AUH | ICE MAKER FISHERY SECTION NOT WORKING | ATTENDED | RANDOLPH | 2
AD COOP/DEYAAR | ABU DHABI | AUH | WATER LEAK FROM C9 CHILLER IN FROZEN SECTION | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | ABU DHABI | AUH | CHILLER C9 WATER LEKAGE | NOT ATTENDED | (blank) | 1
AD COOP/DEYAAR | ABU DHABI | AUH | COMPRESSOR TRIPPING | ATTENDED | RANDOPLH | 1
AD COOP/DEYAAR | AD MALL | AUH | BEVERAGE CHILLER WATER LEAK | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | AD MALL | AUH | CHILLER NOT COOLING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | AD MALL | AUH | DAIRY CHILLER WATER LEAK | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | AD MALL | AUH | F&V SECTION DISPLAY NOISY | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | AD MALL | AUH | ICE MAKER NOT WORKING | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | AD MALL | AUH | RAK SYSTEM FAN NOT WORKING | COMPLETED | TROVEE | 1
AD COOP/DEYAAR | AD MALL | AUH | TABLE TOP CHILLER NOT WORKING | ATTENDED | OLIVER | 1
AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE NOT WORKING | ATTENDED | OLIVER | 2
AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE NOT WORKING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE POWER SWITCH | ATTENDED | OLIVER | 1
AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE POWER TRIPPING | ATTENDED | OLIVER | 2
AD COOP/DEYAAR | ADIB | AUH | ICE MACHINE POWER TRIPPING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | AL MANASIR | AL AIN | FREEZER NO 1 IS NOT WORKING | COMPLETED | TALIB | 1
AD COOP/DEYAAR | AL MINA | AUH | BURNING SMELL FROM FREEZER B51 | COMPLETED | TROVEE/RANDOLPH | 1
AD COOP/DEYAAR | AL MINA | AUH | PLUG IN FREEZER TRIPPING ISSUE. | COMPLETED | TROVEE/RANDOLPH | 1
AD COOP/DEYAAR | AL MINA | AUH | UNIT NO.B29 DOOR NOT CLOSING PROPERLY | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | AL MINA | AUH | B 35 FREEZER TEMP. ISSUE ITEMS ARE MELTING | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | AL ZAHIYA | AUH | CHILLER NOISE ISSUE | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | AWQAF | AUH | 2 FREEZERS ARE NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | AWQAF | AUH | CHEESE CHILLER HIGH TEMP | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | AWQAF | AUH | CHICKEN BREAST FREEZXER f#7 TEMP ISSUE | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | AWQAF | AUH | F&V CHILLER IS NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | AWQAF | AUH | F&V CHILLER NOT WORKING | ATTENDED | FROILAN | 2
AD COOP/DEYAAR | AWQAF | AUH | F&V CHILLER NOT WORKING | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | AWQAF | AUH | F&V CHILLER NOT WORKING | COMPLETED | FROILAN | 2
AD COOP/DEYAAR | AWQAF | AUH | F7 FREEZER HIGH TEMP | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | AWQAF | AUH | FISHERY STORAGE - FAN MOTOR REPLACEMENT | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | AWQAF | AUH | FISHERY STORAGE NOT WORKING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | AWQAF | AUH | FREEZER NOT WORKING / PROMOTION CHILLER WTER LEAK | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | AWQAF | AUH | NEED TO CLEAN THE UNIT | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | AWQAF | AUH | STORE FREEZER TEMP IS NOT WORKING IN BAKERY SECTION | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | AWQAF | AUH | VEG CHILLER STORE WATER LEAK | ATTENDED | OLIVER | 2
AD COOP/DEYAAR | AWQAF | AUH | VEG CHILLER STORE WATER LEAK | COMPLETED | OLIVER | 2
AD COOP/DEYAAR | AWQAF | AUH | VEG CHILLER WATER LEAK | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | AWQAF | AUH | VEG STORAGE NOT WORKING / FISH COLD ROOM HIGH TEMP | COMPLETED | OLIVER | 4
AD COOP/DEYAAR | AWQAF | AUH | VEG. CHILLER POWER OFF | ATTENDED | FROILAN | 6
AD COOP/DEYAAR | AWQAF | AUH | FISH STORE ROOM IS HIGH TEMP. | ATTENDED | TROVEE | 2
AD COOP/DEYAAR | AWQAF | AUH | REPLACE COMPRESSOR | COMPLETED | TROVEE | 3
AD COOP/DEYAAR | AWQAF | AUH | NEED TO CHANGE LIGHT AND FAN MOTOR | ATTENDED | RANDOLPH | 2
AD COOP/DEYAAR | AWQAF | AUH | WATER LEKAGE AT MILK CHILLER C-4 | ATTENDED | FROILAN | 1
AD COOP/DEYAAR | AWQAF | AUH | WATER LEAKAGE FROM MONOBLOCK | ATTENDED | FROILAN | 2
AD COOP/DEYAAR | AWQAF | AUH | WATER LEAKAGE FROM MONOBLOCK | COMPLETED | FROILAN | 2
AD COOP/DEYAAR | AWQAF | AUH | BUTCHERY CHILLER STORE ROOM IS NOT COOLING | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | AWQAF | SHJ | WATER LEAK AT CHEESE DISPLAY C-5 AND VEGETABLE CHILLER DISPLAY | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | BAIN AL JESSRAIN | AUH | CHILLER TRIPPING ISSUE | ATTENDED | OLIVER | 1
AD COOP/DEYAAR | BAIN AL JESSRAIN | AUH | FREEZER NOT WORKING, BUT POWER IS OKAY | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | BAIN AL JESSRAIN | AUH | PROMOTIONAL CHILLER WATER LEAK | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | BANIYAS CENTER | AUH | FREEZER NOT WORKING | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | BIN AL JESSREEN | AUH | BUTCHERY CHILLER HIGH TEMP. | ATTENDED | (blank) | 2
AD COOP/DEYAAR | BIN AL JESSREEN | AUH | FAN MOTOR SOUND IN ROOF TOP | ATTENDED | TROVEE | 1
AD COOP/DEYAAR | BIN AL JESSREEN | AUH | CHILLER NOT WORKING | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | BIN AL JESSREEN | AUH | TABLE TOP CHILLER HIGH TEMP.ISSUE | ATTENDED | OLIVER | 2
AD COOP/DEYAAR | BIN AL JESSREEN | AUH | MEET CHILLER TEMP.ISSUE | ATTENDED | RANDOLPH | 2
AD COOP/DEYAAR | BIN AL JESSREEN | AUH | TWO UNDER COUNTER CHILLER AND FISHERY SECTION ARE NOT WORKING | ATTENDED | (blank) | 2
AD COOP/DEYAAR | BUTEEN | AUH | ALL FREEZER TRIPPING ISSUE | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | BUTEEN | AUH | BAKERY CAKE CHILLER NOISE ISSUE | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | BUTEEN | AUH | CHEESE CHILLER TEMP ISSUE. | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | BUTEEN | AUH | CHEESE OR OLIVE CHILLER NOT COOLING / GLASSDOOR CHEESE CHILLER HIGH TEMP | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | BUTEEN | AUH | ICE CREAM FREEZER NOT COOLING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE ICE NOT FALLING | COMPLETED | IN HOUSE TEAM | 1
AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE NOT WORKING | COMPLETED | FROILAN | 2
AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE NOT WORKING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | BUTEEN | AUH | F 11 FREEZER WATER LEAKAGE | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | BUTEEN | AUH | YOGURTS CHILLER DRIPPING | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE ICE FALLING OUT SIDE | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | BUTEEN | AUH | CHEESE PROMOTION CHILLER HIGH TEMP | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | BUTEEN | AUH | ICE MACHINE NOT WORKING. ICE FALLING OUT SIDE | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | BUTEEN | AUH | CHICKEN FREEZER NOT COOLING ITEMS | (blank) | (blank) | 1
AD COOP/DEYAAR | DANA | AUH | BUTCHERY AND CHEESE CHILLER NOT WORKING | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | DANA | AUH | BUTCHERY CHILLER ICE FORMATION ISSUE | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | DANA | AUH | BUTCHERY CHILLER NOT COOLING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER AND BUCHERY CHILLER TEMP.ISSUE | ATTENDED | RANDOLPH | 2
AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER AND BUCHERY CHILLER TEMP.ISSUE | COMPLETED | OLIVER | 2
AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER AND VEG FREEZER / BUTCHERY DISPLAY CHILLER HIGH TEMP | COMPLETED | FROILAN, OLIVER | 2
AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER AND VEG FREEZER / BUTCHERY DISPLAY CHILLER HIGH TEMP | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER HAVE TOO MUCH ICE INSIDE | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | DANA | AUH | CHEESE CHILLER HIGH TEMP | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | DANA | AUH | COMBI FREEZER NOT COOLING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | DANA | AUH | F&V COLD ROOM CHILLER - REPLACE OF CDU AND EVP | COMPLETED | RANDOLPH, TROVEE, OLIVER | 1
AD COOP/DEYAAR | DANA | AUH | FISH CHILLER WATER LEAK | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | DANA | AUH | FROZEN CHICKEN CHILLER NOT WORKING | COMPLETED | TROVEE | 1
AD COOP/DEYAAR | DANA | AUH | FROZEN VEGETABLE FREEZER TEMP ISSUE | ATTENDED | TROVEE | 1
AD COOP/DEYAAR | DANA | AUH | JUICE AND YOGHURT CHILLER HIGH TEMP | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | DANA | AUH | YOGHURT JUICE AND VEG OPEN CHILLER HIGH TEMP | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | DANA | AUH | FISHERY SECTION CHILLER LEAKAGE | ATTENDED | TROVEE/RANDOLPH | 1
AD COOP/DEYAAR | DANA | AUH | LIGHT NOT WORKING IN FREEZER | ATTENDED | FROILAN | 1
AD COOP/DEYAAR | EMIRATES TOWER | AUH | BUTCHERY STORE TEMP HIGH | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | EMIRATES TOWER | AUH | F&V CHILLER NOISE ISSUE | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | EMIRATES TOWER | AUH | FREEZER NOT WORKING AND SIDE MATERIAL MELTED | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | HAMDAN | AUH | BUTCHERY COLD STORAGE ICE FORMATION / CHILLER WTAER LEAK | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | HAMDAN | AUH | COLD ROOM ICE FORMATION / CHILLER HIGH TEMP | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | HAMDAN | AUH | WATER LEAKAGE | ATTENDED | RANDOLPH | 2
AD COOP/DEYAAR | HAMDAN | AUH | WATER LEAKAGE | COMPLETED | OLIVER | 2
AD COOP/DEYAAR | JADHAF | DXB | FREEZER CABINET F1 TEMP HIGH | ATTENDED | SHAFI | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | BAKERY COLD ROOM - REPLACEMENT OF FAN MOTOR AND REF CHARGING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | BREAKER FALIUR | COMPLETED | RANDOLPH | 3
AD COOP/DEYAAR | KHALIFA CITY | AUH | COMPRESSOR MAIN CONTROLLER HIGH READING DISPLAY | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | DRINKS CHILLER NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | F#10 & F#11 FREEZER TEMP NOT GOOD | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | F1 WALK IN FREEZER NO POWER | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER COMPRESSOR READING NOT OKAY | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER DOOR GASKET IS DAMAGED | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER RACK UNIT NOT WORKING | COMPLETED | RANDOLPH | 6
AD COOP/DEYAAR | KHALIFA CITY | AUH | BAKERY CHILLER TEMP ISSUE | NOT ATTENDED | (blank) | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER NO.4 NOT WORKING | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | PLUGE IN DISPLAY CHILLER SHOWING ALARM | ATTENDED | FROILAN | 1
AD COOP/DEYAAR | KHALIFA CITY | AUH | FREEZER NO 7 TEMP ISSUE | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | MADINAT ZAYED | AUH | ALL FREEZER NOT WORKING | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | MADINAT ZAYED | AUH | CHILLER LIGHT NOT WORKING | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | MADINAT ZAYED | AUH | COLD ROOM ICE FORMATION | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | MADINAT ZAYED | AUH | DISPLAY CHILLER WATER LEAK | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MADINAT ZAYED | AUH | FREEZER NO 1 UNUSUAL SOUND | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | MADINAT ZAYED | AUH | CHILLER WATER LEAKAGE | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | MADINAT ZAYED | AUH | CHILLER TRIPPING ISSUE | (blank) | (blank) | 1
AD COOP/DEYAAR | MBZ | AUH | BAKERY CHILLER NOT WORKING | COMPLETED | OLIVER | 2
AD COOP/DEYAAR | MBZ | AUH | BAKERY CHILLER NOT WORKING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | MBZ | AUH | COMBI FREEZER HIGH TEMP | COMPLETED | OLIVER | 2
AD COOP/DEYAAR | MBZ | AUH | COMBI FREEZER HIGH TEMP - REPLACE,ENT OF FAN MOTOR AND REF CHARGING | COMPLETED | OLIVER | 2
AD COOP/DEYAAR | MBZ | AUH | COMBI FREEZER NOT WORKING | COMPLETED | OLIVER | 2
AD COOP/DEYAAR | MBZ | AUH | COMBI FREEZER NOT WORKING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | MBZ | AUH | FREEZER F#22 HIGH TEMP | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MBZ | AUH | FREEZER HIGH TEMP | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | MBZ | AUH | FREEZER NOT WORKING COMPRESSOR ROOM ABNORMAL NOISE ISSUE | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | MBZ | AUH | ICE FORMATION IN THE INSULATION | ATTENDED | RANDOLPH | 3
AD COOP/DEYAAR | MBZ | AUH | ICE FORMATION IN THE INSULATION | COMPLETED | OLIVER | 3
AD COOP/DEYAAR | MBZ | AUH | ICE FORMATION IN THE INSULATION | COMPLETED | RANDOLPH | 3
AD COOP/DEYAAR | MBZ | AUH | INSULATION REPLACEMNET FOR THE FREEZER REF LINES | COMPLETED | ROGER | 1
AD COOP/DEYAAR | MBZ | AUH | WATER LEAK | (blank) | (blank) | 1
AD COOP/DEYAAR | MBZ | AUH | FREEZER NOT WORKING | COMPLETED | RANDOPLH | 1
AD COOP/DEYAAR | MBZ | AUH | NO AIR FLOW IN BED FREEZER | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | MBZ | AUH | WATER LEAK IN CHILLER | COMPLETED | TROVEE | 1
AD COOP/DEYAAR | MEGAMALL MEGAMART | SHJ | BUTCHERY CHILLER HIGH TEMP. | ATTENDED | VIGNESH | 2
AD COOP/DEYAAR | MEGAMALL MEGAMART | SHJ | BUTCHERY CHILLER HIGH TEMP. | COMPLETED | AHSAN | 2
AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | FREZEER TEMP OK BUT ITEMS MELTING | COMPLETED | VIGNESH | 1
AD COOP/DEYAAR | MEGAMART AL NADHA | SHJ | CHILLER NO 4 TRIPPING UNIT | ATTENDED | VIGNESH | 1
AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | 3 CHILLER CABINET HIGH TEMP | COMPLETED | VIGNESH | 2
AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | CABINET SHIFTING AND INSTALLATION | COMPLETED | DENNIS, ROGER | 1
AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | CHILLER CABINET REFRIGERANT CHARGING | COMPLETED | MOHAMMED | 1
AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | DELICATE SECTION LEAK FIXING AND REFILLING GAS | COMPLETED | AHSAN | 2
AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | FREEZER TEMP ISSUE | ATTENDED | SADAM | 1
AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | OPEN CHILELR WATER LEAK | COMPLETED | AHSAN | 1
AD COOP/DEYAAR | MEGAMART AL NADHA | DXB | VEG CHILLER NOT WORKING | ATTENDED | MOHAMMED | 1
AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | BAKERY DISPLAY NOT WORKING | ATTENDED | AHSAN | 1
AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | BAKERY SECTION CHILLER HIGH TEMP | ATTENDED | VIGNESH | 1
AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | FREEZER NOT COOLING | ATTENDED | AHSAN | 1
AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | FREEZER TEMP ISSUE | ATTENDED | AHSAN | 1
AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | VEGETABLE FREEZER NOT WORKING | ATTENDED | VIGNESH | 1
AD COOP/DEYAAR | MEGAMART MEGAMALL | SHJ | COLD ROOM TRIPPING ISSUE | (blank) | (blank) | 1
AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | DOUBLE DOOR VERTICAL CHILLER HIGH TEMP | COMPLETED | VIGNESH | 1
AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | EVAPORATORE FAN SOUND | ATTENDED | RACEL | 1
AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | FAN MOTOR AVAILABLE IN STORE | ATTENDED | VIGNESH | 2
AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | PLUGIN CHILLER TRIPPING ISSUE | ATTENDED | VIGNESH | 2
AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | WATER LEAKAGE | ATTENDED | AHSAN | 2
AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | WATER LEAKAGE | ATTENDED | (blank) | 2
AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | CHEESE COUNTER CHILLER IS NOT WORKING | COMPLETED | AHSAN | 1
AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | FROZEN FREEZER NOT WORKING | ATTENDED | SABITH ALI | 1
AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | FREEZER CABINETS ARE NOT WORKING | COMPLETED | RACEL | 1
AD COOP/DEYAAR | MINA | AUH | 2 ICE MACHINES NOT WORKING | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | MINA | AUH | B21 CHILLER NOISE ISSUE | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | B34 FREEZER NOT COOLING | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | MINA | AUH | BUTCHERY CHILLER HIGH TEMP | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | CHILLER B 22 MAKING SOUND | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | CHILLER CONDENSER FAN MOTOR FAN TRIPPING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | CHILLER NOT COOLING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | COLD ROOM EVP UNIT ICE FORMATION | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | F&V FREEZER NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | FREEZER B34 NOT COOLING / CHEESE CHILLER NOT COOLING | ATTENDED | OLIVER | 1
AD COOP/DEYAAR | MINA | AUH | FREEZER B38 NOT COOLING | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | FREEZER B38 NOT COOLING, ITEMS ARE MELTING | ATTENDED | RANDOLPH | 3
AD COOP/DEYAAR | MINA | AUH | FREEZER NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | FREEZER#2 HIGH IN RECEIVING AREA 2 | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | FREEZER#2 HIGH TEMP | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | MINA | AUH | FREEZER#5 NOT COOLING | COMPLETED | RANDOLPH | 3
AD COOP/DEYAAR | MINA | AUH | FREZZER B38 NOT COOLING | COMPLETED | RANDOLPH | 3
AD COOP/DEYAAR | MINA | AUH | ICE MACHINE NOT WORKING | ATTENDED | FROILAN | 2
AD COOP/DEYAAR | MINA | AUH | ICE MACHINE NOT WORKING | COMPLETED | FROILAN | 2
AD COOP/DEYAAR | MINA | AUH | INSULATION WORK | COMPLETED | ROGER | 109
AD COOP/DEYAAR | MINA | AUH | MINA INDULLATION REPLACEMNET WORK | COMPLETED | DENNIS, ROGER | 9
AD COOP/DEYAAR | MINA | AUH | PROOFER TEMP.ISSUE | NOT ATTENDED | (blank) | 1
AD COOP/DEYAAR | MINA | AUH | RAW VEG CHILLER ICE FORMATION / READY TO EAT CHILLER HIGH TEMP | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | AUH | FREEZER B35 NOT WORKING | ATTENDED | OLIVER | 1
AD COOP/DEYAAR | MINA | AUH | CHILLER NOT WORKING NO 07 | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | DXB | B31 UPRIGHT FREEZER SOUND COMING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MINA | DXB | HEAVY DUST ACCUMULATION ON THE WALIN CHILELR GUARD | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MUROOR | AUH | BAKERY FREEZER NOT WORKING | ATTENDED | OLIVER | 1
AD COOP/DEYAAR | MUROOR | AUH | CHEESE STORAGE CHILLER NOT WORKING | ATTENDED | RANDOLPH | 2
AD COOP/DEYAAR | MUROOR | AUH | CHILLER NOT COOLING | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | MUROOR | AUH | CHILLER ROOFTOP MAKING UNUSAL NOISE | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | MUROOR | AUH | F&V COLDR OOM FAN GUARD WITH HEAVY DUST ACCUMULATION NEED DEEP CLEANING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MUROOR | AUH | GAS LEAK IN THE CHEESE SECTION | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | MUROOR | AUH | ICE FORMATION | ATTENDED | OLIVER | 2
AD COOP/DEYAAR | MUROOR | AUH | ICE MACHINE WATER LEAK | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MUROOR | AUH | SMALL CHILLER DISPLAY IN THE FISH SECTION IS NOT WORKING | (blank) | (blank) | 1
AD COOP/DEYAAR | MUROOR | AUH | BUTCHERY WALK IN CHILLER TRIPPED 3 TIMES | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | MUROOR | AUH | CHEESE CHILLER STORAGES NOT WORKING PROPERLY | ATTENDED | (blank) | 2
AD COOP/DEYAAR | MUROOR | AUH | FAN MOTOR CHANGE | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | MUROOR | AUH | BUTCHERY COLD ROOM MONOBLOCK ICE FORMATION | ATTENDED | FROILAN | 1
AD COOP/DEYAAR | SE 13 | AUH | GAS CHARGED | COMPLETED | RANDOLPH | 3
AD COOP/DEYAAR | SE 13 | AUH | ICE CREAMFREEZER DEFROST FROM LONG TIME | ATTENDED | TROVEE | 3
AD COOP/DEYAAR | SE 13 | AUH | ICE CREAMFREEZER DEFROST FROM LONG TIME | ATTENDED | (blank) | 3
AD COOP/DEYAAR | SE 13 | AUH | FREEER TEMP ISSUE. NO.1 | ATTENDED | FROILAN | 2
AD COOP/DEYAAR | SE 13 | AUH | GAS CHARGING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | SE13 | AUH | CHEESE CHILLER DISPLAY WATER LEAK | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | SHAMKHA | AUH | CHEESE CHILLER HIGH TEMP | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SHAMKHA | AUH | CHEESE CHILLER TEMP ISSUE. | ATTENDED | (blank) | 1
AD COOP/DEYAAR | SHAMKHA | AUH | CHILLER NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SHAMKHA | AUH | CHILLER WATER LEAK | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SHAMKHA | AUH | F & V CHILLER NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SHAMKHA | AUH | FREEZER HIGH TEMP | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SHAMKHA | AUH | ICE MACHINE NOT WORKING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | SHAMKHA | AUH | ICE MACHINE NOT WORKING | NOT ATTENDED | (blank) | 2
AD COOP/DEYAAR | SHAMKHA | AUH | VEG CHILLER IS NOT WORKING | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | SHAMKHA | AUH | TABLE CHILLER HIGH TEMP.ISSUE | ATTENDED | TROVEE | 2
AD COOP/DEYAAR | SHAMKHA | AUH | TABLE CHILLER HIGH TEMP.ISSUE | ATTENDED | (blank) | 2
AD COOP/DEYAAR | SHAMKHA | AUH | DOOR IS CLOSING PROPERLY ICE CREAM FREEZER | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | SHAMKHA | AUH | BUTCHERY SECTION FREEZER NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SHAMKHA | DXB | FRUITS DISPLAY CHILELR NOT COOLING / CHILLER STORE WATER LEAK | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | SHAMKHA | AUH | CHILLER AREA TEMP HIGH | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | SHAMKHA | AUH | ICE CREAM FREEZER TEMP ISSUE | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SHAMKHA | AUH | INSTALLATION OF ICE MACHINE / ICE CREAM FREEZER IS NOT WORKING | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | SHAMKHA | AUH | PLUS RANGE SYSTEM REF CHARGING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | SPAR ADIA C 18 | AUH | DAMAGED GLASS DOOR OF CHILLER | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | SPAR ELECTRA | AUH | EGG CHILLER NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SPAR ELECTRA | AUH | FREEZER ICE FORMATION | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | F&V CHILLER WATER LEAK | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | F&V STORE CHILLER WATER LEAK | (blank) | (blank) | 1
AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | FREEZER TEMP ISSUE. | ATTENDED | TROVEE | 2
AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | BUTCHERY CHILLER NOT WORKING | ATTENDED | TROVEE | 2
AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | BUTCHERY CHILLER NOT WORKING | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | CONDENSOR FAN MOTOR NOT WORKING | COMPLETED | TROVEE | 1
AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | COMBI FREEZER TEMP ISSUE | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | WATER LEAKAGE IN FREEZER | ATTENDED | FROILAN | 1
AD COOP/DEYAAR | SPAR KHALIDIYA | AUH | WATER LEAKAGE FROM F&V CHILLER | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | SPAR OMEGA | AUH | COLD DRINK CHILLER NOT WORKING | ATTENDED | RANDOLPH | 1
AD COOP/DEYAAR | SPAR SAADIAYT | AUH | BAKERY AND HOT MEAT DISPLAY CHILLER TRIP ISSUE. | COMPLETED | OLIVER | 1
AD COOP/DEYAAR | SPAR SAADIAYT | AUH | CHEESE SECTION CHILLER TEMP ISSUE | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | SPAR SAADIAYT | AUH | CHEESE SECTION SHUT DOWN | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SPAR SAADIYAT | AUH | CHEESE CHILLER HIGH TEMP | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | SPAR SAADIYAT | AUH | CHEESE CHILLER NOT WORKING | ATTENDED | RANDOLPH | 2
AD COOP/DEYAAR | SPAR SAADIYAT | AUH | VEG CHILLER NOT WORKING | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | SPAR SHABAT PLAZA | AL AIN | STORE FREEZER NOT WORKING | ATTENDED | TALIB | 2
AD COOP/DEYAAR | SPAR SHABHAT PLAZA | AL AIN | FREEZER NO 05 TEMP.ISSUE | COMPLETED | TALIB | 1
AD COOP/DEYAAR | SPAR SHABHAT PLAZA | AL AIN | WATER LEAKING FROM OPEN CHILLER NO.3 | ATTENDED | TALIB | 1
AD COOP/DEYAAR | SPAR ZAKHER MALL | AL AIN | MONTHLY REPORT | COMPLETED | TALIB | 4
AD COOP/DEYAAR | SPAR ZAKHER MALL | AUH | DISPLAY FREEZER NOT COLLING | (blank) | (blank) | 1
AD COOP/DEYAAR | ZAYED 1ST | AUH | BUTCHERY COLD ROOM STORAGE UNIT ICE FORMATION | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | ZAYED 1ST | AUH | BUTCHERY CHILLER NOT WORKING | COMPLETED | FROILAN | 1
AD COOP/DEYAAR | ZAYED 1ST | AUH | TUBE LIGHTS NOT WORKING IN FREEZER | COMPLETED | RANDOLPH | 1
AD COOP/DEYAAR | ZAYEST 1ST | AUH | ICE FORMING IN THE STORAGE FREEZER | ATTENDED | FROILAN, OLIVER | 1
AD COOP/DEYAAR | SPAR EXPRESS OMEGA TOWER | AUH | CHILLER WATER LEAK | COMPLETED | TROVEE | 1
AD COOP/DEYAAR | SPAR EXPRESS OMEGA TOWER | AUH | VEGETABLE CHILLER MAKING SOUND | ATTENDED | RANDOLPH | 2
AD COOP/DEYAAR | SPAR EXPRESS OMEGA TOWER | AUH | VEGETABLE CHILLER MAKING SOUND /FAN CHANGING | COMPLETED | RANDOLPH | 2
AD COOP/DEYAAR | ZAKHER MALL | AL AIN | FREEZER TEMP.ISSUE | COMPLETED | TALIB | 1
AD COOP/DEYAAR | ZAKHER MALL | AUH | DISPLAY FREEZER NOT COLLING | COMPLETED | TALIB | 1
AD COOP/DEYAAR | KHALIDIYA GARDEN | AUH | BAKERY CHILLER WATER LEAKAGE 1 & 2 NO CHILLER | COMPLETED | RANDOLPH | 1
ADASI | ABU DHABI | AUH | FREEZER COLD ROOM NOT COOLING | COMPLETED | RANDOLPH | 1
ADNOC | 330 | SHJ | ICE MACHINE NOT WORKING | COMPLETED | VIGNESH | 1
ADNOC | 384 | DXB | FREEZER CABINET NOT WORKING PROPERLY | COMPLETED | SADAM | 1
ADNOC | 435 | RAK | VERTICAL FREEZER HIGH TEMP | COMPLETED | RACEL | 1
ADNOC | 448 | AUH | CHILLER TEMP. ISSUE | COMPLETED | RANDOLPH | 1
ADNOC | 448 | AUH | WATER LEAK FROM CHILLER CABINET | COMPLETED | RANDOLPH | 1
ADNOC | 511 | SHJ | HOT DOG GRILLER AND AND ROLLER DELIVERY | COMPLETED | VIGNESH | 1
ADNOC | 523 | AUH | CONVOTHERM NOT WORKING | (blank) | (blank) | 1
ADNOC | 596 | FUJ | FREEZER HIGH TEMP AND ITEMS ARE MELTING | ATTENDED | SABITH ALI | 2
ADNOC | 596 | FUJ | FREEZER HIGH TEMP AND ITEMS ARE MELTING | COMPLETED | VIGNESH | 2
ADNOC | 596 | FUJ | FREEZER NOISE ISSUE | COMPLETED | SABITH ALI | 2
ADNOC | 596 | FUJ | NOISY FUNCTION OF COND FAN MOTOR | COMPLETED | RACEL | 2
ADNOC | 634 | SHJ | HOT DOG GRILLER NOT WORKING | COMPLETED | ALLAN | 1
ADNOC | 634 | SHJ | ICE MACHINE WATER LEAK | ATTENDED | SABITH ALI | 3
ADNOC | 634 | SHJ | ICE MACHINE WATER LEAK | COMPLETED | AHSAN | 3
ADNOC | 634 | SHJ | ICE MACHINE WATER LEAK | COMPLETED | SABITH ALI | 3
ADNOC | 634 | SHJ | WATER LEAK FROM FILTER | COMPLETED | AHSAN | 1
ADNOC | 750 | FUJ | 2 OPEN CHILLER NOT COOLING | COMPLETED | RACEL | 2
ADNOC | 750 | FUJ | GLASS DOOR CHILLER HIGH TEMP. | COMPLETED | RACEL | 1
ADNOC | 750 | FUJ | HIGH TEMP. | ATTENDED | RACEL | 2
ADNOC | 750 | FUJ | OPEN CHILLER LIGHT NOT WORKING | ATTENDED | VIGNESH | 1
ADNOC | 750 | FUJ | STELL BODY FREEZER NOT WORKING | COMPLETED | RACEL | 1
ADNOC | 750 | FUJ | TEMP.ISSUE | COMPLETED | VIGNESH | 1
ADNOC | 794 | AUH | WALKIN FREEZER NOT WORKING | COMPLETED | RANDOLPH | 1
ADNOC | 885 | FUJ | ICE MACHINE NOT WORKING | COMPLETED | VIGNESH | 1
ADNOC | 917 | AUH | FREEZER TEMP ISSUE. ICE CREAM TEMP ISSUE. | COMPLETED | RANDOLPH | 1
ADNOC | 227 | DXB | ICE MACHINE COMPLENT | COMPLETED | MOHAMMED | 1
ADNOC | 173 | AUH | BAKERY CHILLER CLEAN | NOT ATTENDED | (blank) | 1
ADNOC | 639 | AUH | HOT GRILLER NOT WORKING | COMPLETED | ALLAN | 1
AL AIN COOP | AL MANASIR | AL AIN | FREEZER GLASS DOOR ISSUE, OPENS AUTOMATICALLY | COMPLETED | VIGNESH | 1
AL FALAJ | ABU HAIL | DXB | BLOWER INSTALLATION | ATTENDED | ABID, AJMEER | 1
AL FALAJ | ABU HAIL | DXB | UIT ROOM AC NOT WORKING | ATTENDED | SARAVANAN | 1
AL FALAJ | ABU HAIL | SHJ | CHILLER NO.3 TEMP ISUUE | COMPLETED | AHSAN | 1
AL MASA | KIZAD | AUH | 8 COLD ROOM NEED TO BE START | COMPLETED | OLIVER | 1
AMAZON | DXB 3 | AUH | Q1 | COMPLETED | ABID | 37
AMAZON | DXB 3 | DXB | PPM | COMPLETED | ABID | 74
AMAZON | DXB 3 | DXB | Q1 | COMPLETED | ABID | 111
AMAZON | DXB 3 | DXB | Q 1 PPM | COMPLETED | ABID | 1
AMAZON | DXB 3 | DXB | PPM Q 1 | COMPLETED | ABID | 1
AMAZON | DXB 3 | DXB | PPM Q 1 | COMPLETED | GOVIND/ABID | 1
AMAZON | DXB 3 | DXB | PPM DONE Q 1 | COMPLETED | ABID | 1
AMAZON | DXB 5 | DXB | HAMZAT ROOM TEMPURATURE ISSUE | COMPLETED | ABID | 1
AMAZON | (blank) | AUH | PPM | COMPLETED | KALAMUDIN | 1
AMAZON | AUH | AUH | PPM | COMPLETED | KALAMUDIN | 0
AMAZON | AUH 1 | AUH | FCU FAULT | COMPLETED | ANWER | 1
ANSAR | KARAMA | DXB | BUTCHERY CHILLER WATER LEAK / LIGHT NOT WORKING IN THE READY TO GO CHILLER | ATTENDED | SHAFI | 2
ANSAR | KARAMA | DXB | CHILLER ROOM ICE FORMATION | ATTENDED | SARAVANAN | 1
ANSAR | KARAMA | DXB | COLD ROOM WATER LEKA AND ICE FORMATION | COMPLETED | MOHAMMED | 1
ANSAR | KARAMA | DXB | COMBI FREEZER WATER LEAK | COMPLETED | SADAM | 1
ANSAR | KARAMA | DXB | FREEZER COLD ROOM HIGH TEMP | ATTENDED | SABITH ALI | 2
ANSAR | KARAMA | DXB | FREEZER COLD ROOM TRMP. ISSUE | ATTENDED | MOHAMMED | 2
ANSAR | KARAMA | DXB | FREEZER WATER LEAK | COMPLETED | SADAM | 1
ANSAR | KARAMA | DXB | HOT FOOD CHILLER HIGH TEMP | COMPLETED | SARAVANAN | 1
ANSAR | KARAMA | DXB | KICTHEN UNITS ARE NOT WORKING | COMPLETED | RACEL | 1
ANSAR | KARAMA | DXB | LIGHT REPLACEMENT IN READY TO GO CHILLER | COMPLETED | SARAVANAN | 2
ANSAR | KARAMA | DXB | LIGHTS NEED TO REPLACE FOR READY TO GO CHILLER | COMPLETED | SADAM | 1
ANSAR | KARAMA | DXB | MEAT CHILLER TEMP.ISSUE | COMPLETED | SABITH ALI | 1
ANSAR | KARAMA | DXB | NEED TO CHANDE CONDENSOR FAN MOTOR | ATTENDED | SABITH ALI | 1
ANSAR | KARAMA | DXB | READY TO EAT SECTION LIGHT NOT WORKING | COMPLETED | SARAVANAN | 1
ANSAR | KARAMA | DXB | VEG OPEN CHILLER WATER LEAK | COMPLETED | MOHAMMED | 1
ANSAR | KARAMA | DXB | WATER LEAK | ATTENDED | MOHAMMED | 2
ANSAR | KARAMA | DXB | WATER LEAK | ATTENDED | (blank) | 2
ANSAR | KARAMA | DXB | WATER LEAK FROM FREEZER | ATTENDED | AHSAN | 2
ANSAR | KARAMA | DXB | WATER LEAK FROM FREEZER | ATTENDED | MOHAMMED | 2
ANSAR | KARAMA | DXB | FREEZER UNIT SHUT OFF | ATTENDED | AHSAN | 3
ANSAR | KARAMA | DXB | WATER LEAKAGE FROM DELI CHILLER AND VEGETABLE DISPLAY | COMPLETED | VIGNESH | 1
ANSAR | KARAMA | DXB | COMBI FREEZER TEMP ISSUE | ATTENDED | SHABEEB | 3
ANSAR | KARAMA | DXB | BACK STORE ROOM WATER LEAKAGE | COMPLETED | SARAVANAN | 1
ANSAR | KARAMA | DXB | ALL CHILLER SHUTDOWN | ATTENDED | AHSAN | 1
ANSAR | KARAMA | DXB | CHILLER WATER LEAK | COMPLETED | RACEL | 1
ANSAR | KARAMA | DXB | COLD ROOM LIGHT NOT WORKING | ATTENDED | SARAVANAN | 1
ANSAR | KARAMA | DXB | COMBI FREEZER NOT COOLING | COMPLETED | AHSAN | 1
ANSAR | KARAMA | DXB | FREEZER LIGHT NOT WORKING | ATTENDED | AHSAN | 4
ANSAR | KARAMA | DXB | ICE CREEM FREEZER SHUTDOWN | COMPLETED | SABITH ALI | 3
ANSAR | KARAMA | SHJ | COMBI FREEZER NOT WORKING | COMPLETED | SHAFI | 1
BADIA FARMS | AL QUOZ | DXB | ZONE 3 CHILLER NOT WORKING | ATTENDED | (blank) | 2
BADIA FARMS | AL QUOZ | DXB | ZONE 3 CHILLER NOT WORKING | COMPLETED | MOHAMMED | 2
BADIA FARMS | AL QUOZ | DXB | COMPRESSOR REMOVAL BY CRANE | COMPLETED | SARAVANAN | 1
BANAYA FORREST | BLUE WATER | DXB | PPM FOR KITCHEN HOOD | COMPLETED | ABID, AJMEER | 37
BANIYAS COOP | BANIYAS CENTER | AUH | EGG CHILLER PLEASE CHECK (FUNGUS / RUSTED) | COMPLETED | RANDOLPH | 1
BANIYAS COOP | BANIYAS CENTER | AUH | UNIT HIGH TEMP. | ATTENDED | FROILAN | 1
BANIYAS COOP | SARAB | AUH | BAKERY CHILLER NOT WORKING | COMPLETED | RANDOLPH | 1
BANIYAS COOP | SARAB | AUH | BUTCHERY CHILLER TRIPPING ISSUE | COMPLETED | RANDOLPH | 1
BANIYAS COOP | SARAB | AUH | CAKE CHILLER TEMP ISSUE | ATTENDED | RANDOLPH | 2
BANIYAS COOP | SARAB | AUH | CAKE CHILLER TEMP ISSUE | COMPLETED | RANDOLPH | 2
BANIYAS COOP | SARAB | AUH | CAKE DISPLAY NEED TO CHECK | COMPLETED | RANDOLPH | 1
BANIYAS COOP | SARAB | AUH | ISLAND FREEZER HIGH TEMP | COMPLETED | RANDOLPH | 1
BANIYAS COOP | SARAB | AUH | FREEZER HIGHT TEMP. | ATTENDED | RANDOLPH | 2
BANIYAS COOP | SARAB | AUH | FREEZER COLD ROOM NOT WORKING | ATTENDED | RANDOLPH | 2
BANIYAS COOP | SARAB | DXB | CHEESE SECTION CHILLER NOT WORKING | COMPLETED | FROILAN | 1
BANIYAS COOP | SHAHAMA | AUH | CHILLER TEMP ISSUE. | ATTENDED | RANDOLPH | 2
BANIYAS COOP | SHAHAMA | AUH | FREEZER NOT WORKING | ATTENDED | RANDOLPH | 1
BANIYAS COOP | SHAHAMA | AUH | FREEZER TEMP.ISSUE AND SOUND IN UNIT | COMPLETED | FROILAN | 1
BANIYAS COOP | SHAHAMA | AUH | CHILLER TEMP ISSUE./EGG CHILLER CHANGING COMPRESSOR | COMPLETED | RANDOLPH | 2
BANYA FORREST | BLUE WATER | DXB | KITCHEN AC IS DOWN NOT WORKING | ATTENDED | MOHAMMED | 1
BAQER MOHEBI | ABU HAIL | DXB | CDU#6 FAN MOTOR NOT WORKING | COMPLETED | RACEL | 2
BAQER MOHEBI | ABU HAIL | DXB | CDU#6 FAN MOTOR NOT WORKING | COMPLETED | SABITH ALI | 2
BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER HEAD NOT COOLING | COMPLETED | VIGNESH | 1
BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER HEADER NO COOLING | COMPLETED | AHSAN | 1
BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER NO COOLING | COMPLETED | AHSAN | 3
BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER NO COOLING | COMPLETED | DENNIS | 3
BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER NO COOLING | COMPLETED | SABITH ALI | 3
BAQER MOHEBI | ABU HAIL | SHJ | COMBI FREEZER NO COOLING | COMPLETED | VIGNESH | 1
BAQER MOHEBI | ABU HAIL | SHJ | COMBI FREEZER TEMP ISSUE | ATTENDED | SABITH ALI | 1
BAQER MOHEBI | ABU HAIL | SHJ | FREEZER LIGHT NOT WORKING | ATTENDED | AHSAN | 1
BAQER MOHEBI | ABU HAIL | DXB | CHEESE AND MILK CHILLER WATER LEAK AND LIGHT NOT WORKING | COMPLETED | AHSAN | 1
BAQER MOHEBI | ABU HAIL | DXB | COMBI FREEZER NOT WORKING | COMPLETED | RACEL | 1
BAQER MOHEBI | ABU HAIL | DXB | VEG CHILLER HIGH TEMP | COMPLETED | AHSAN | 1
BAQER MOHEBI | AL NADHA | DXB | COLD ROOM COMPRESSOR SOUND | ATTENDED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | DXB | COMBI FREEZER PORK SECTION | COMPLETED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | DXB | SOUND FROM CHEESE CHILLER | COMPLETED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | SHARJAH | ICE CREAM FREEZER NOT WORKING | COMPLETED | MOHAMMED | 1
BAQER MOHEBI | AL NADHA | SHJ | CHEESE COLD ROOM TEMP ISSUE. | COMPLETED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER LIGHT NOT WORKING | COMPLETED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER NOISE ISSUE(CH-18) | COMPLETED | SABITH ALI | 1
BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER TRIPPING ISSUE | ATTENDED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | SHJ | BUTCHERY CHILLER HIGH TEMP. | COMPLETED | SABITH ALI | 1
BAQER MOHEBI | AL NADHA | SHJ | BUTCHERY DISPLAY LIGHTS CHILLER NOT WORKING | COMPLETED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | SHJ | CHILLER TEMP ISSUE | COMPLETED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | SHJ | MILK CHILLER WATER LEAK | ATTENDED | VIGNESH | 2
BAQER MOHEBI | AL NADHA | SHJ | MILK CHILLER WATER LEAK | COMPLETED | VIGNESH | 2
BAQER MOHEBI | AL NADHA | DXB | PORK FREEZER NOT WORKING | COMPLETED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | DXB | TABLE TOP CHILELR DOOR ISSUE | ATTENDED | AHSAN | 2
BAQER MOHEBI | AL NADHA | DXB | TABLE TOP CHILELR DOOR ISSUE | COMPLETED | AHSAN | 2
BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILELR NO COOLING / COLD ROOM CHILELR NOT WORKING | COMPLETED | SARAVANAN | 2
BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER COMPRESSOR INSTALLATION | COMPLETED | VIGNESH | 2
BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER GALSS DAMAGE | COMPLETED | VIGNESH | 1
BAQER MOHEBI | AL NADHA | SHJ | BAKERY CHILLER NOT WORKING | COMPLETED | AHSAN | 1
BAQER MOHEBI | AL NADHA | SHJ | CHILLER LIGHT NOT WORKING | COMPLETED | AHSAN | 1
BAQER MOHEBI | AL NADHA | SHJ | FREEZER ROCKER SWITCH DAMAGE | COMPLETED | AHSAN | 1
BAQER MOHEBI | AL NAHDA | DXB | BUTCHERY TABLE TOP CHILLER NOT WORKING | COMPLETED | AHSAN | 1
BAQER MOHEBI | AL NAHDA | DXB | F& V CHILLER NOT WORKING | ATTENDED | VIGNESH | 1
BAQER MOHEBI | AL NAHDA | SHJ | BAKERY CHILLER NOT WORKING NO 18 | ATTENDED | RACEL | 1
BAQER MOHEBI | AL NAHDA | SHJ | ISLAND FREEZER TRIPPING | ATTENDED | AHSAN | 1
BAQER MOHEBI | BUR DUBAI | DXB | CHILLER HIGH TEMP. VEG CHILLER LIGHT NOT WORKING | COMPLETED | MOHAMMED | 1
BAQER MOHEBI | BUR DUBAI | DXB | CHILLER NAD FREEZER LIGHT NOT WORKING | COMPLETED | MOHAMMED | 1
BAQER MOHEBI | BUR DUBAI | DXB | CHILLER NOT WORKING | COMPLETED | MOHAMMED | 2
BAQER MOHEBI | BUR DUBAI | DXB | CHILLER TEMP. ISSUE | COMPLETED | AHSAN | 1
BAQER MOHEBI | BUR DUBAI | DXB | LEAF CHILLER TEMP ISSUE | COMPLETED | VIGNESH | 1
BAQER MOHEBI | BUR DUBAI | DXB | MILK AND JUICE CHILLER NOT WORKING | COMPLETED | SHAFI | 2
BAQER MOHEBI | BUR DUBAI | DXB | MILK CHILLER NOT COOLING | ATTENDED | SHAFI | 2
BAQER MOHEBI | BUR DUBAI | DXB | REPLACEMENT OF CONDENSER FAN MOTOR | COMPLETED | SABITH ALI | 2
BAQER MOHEBI | BUR DUBAI | DXB | VEG CHILLER 6 NOS LIGHT NOT WORKING | COMPLETED | AHSAN | 1
BAQER MOHEBI | BUR DUBAI | DXB | VEG CHILLER NOT COOLING | COMPLETED | SADAM | 1
BAQER MOHEBI | BUR DUBAI | DXB | VEG CHILLER TRIPPING | COMPLETED | SADAM | 1
BAQER MOHEBI | BUR DUBAI | DXB | MILK CHILLER COOLING ISSUE. | COMPLETED | VIGNESH | 1
BAQER MOHEBI | BUR DUBAI | DXB | LEAF CHILLER NOT WORKING | COMPLETED | SADAM | 1
BAQER MOHEBI | BUR DUBAI | DXB | BAKERY CHILLRE NOT COOLING | COMPLETED | MOHAMMED | 1
BAQER MOHEBI | BUR DUBAI | DXB | MILK CHILLER HIGH TEMP. | (blank) | (blank) | 1
BAQER MOHEBI | BUR DUBAI | DXB | EGG & JUICE CHILLER TRIPPING ISSUE | COMPLETED | SARAVANAN | 4
BAQER MOHEBI | BUR DUBAI | DXB | EGG CHILLER LIGHT NEED TO REPLACE / ISLAND FREEZER LIGHT NEED TO REPLACEMENT | ATTENDED | SARAVANAN | 1
BAQER MOHEBI | SATWA | DXB | BAKERY CHILLER NOT WORKING | COMPLETED | SHABEEB | 1
BAQER MOHEBI | SATWA | DXB | BAKERY CHILLER TRIPPING | COMPLETED | RACEL | 1
BAQER MOHEBI | SATWA | DXB | CHILLER 4 FEET WARM WHITE NOT WORKING | COMPLETED | SADAM | 1
BAQER MOHEBI | SATWA | DXB | FAN MOTOR NOISE ISSUE | COMPLETED | SHAFI | 1
BAQER MOHEBI | SATWA | DXB | JICE AND WATER CHILLER WATER LEAK | COMPLETED | RACEL | 1
BAQER MOHEBI | SATWA | DXB | NEED TO CHANGE LIGHT WITH FRAME IN BAKERY SECTION | ATTENDED | AHSAN | 2
BAQER MOHEBI | SATWA | DXB | NEED TO CHANGE LIGHT WITH FRAME IN BAKERY SECTION | NOT ATTENDED | (blank) | 2
BAQER MOHEBI | SATWA | DXB | ICE CREAMFREEZER HIGH TEMP. | COMPLETED | AHSAN | 1
BAQER MOHEBI | SATWA | DXB | LIGHTS NOT WORKING | NOT ATTENDED | (blank) | 1
BAQER MOHEBI | VILLA | DXB | COLD ROOM WATER LEAK | COMPLETED | SARAVANAN | 1
BAQER MOHEBI | WAREHOUSE | DXB | CHILLER UNITY POWER TRIPPING | ATTENDED | SHAFI | 4
BAQER MOHEBI | WAREHOUSE | DXB | CHILLER NOT WORKING | COMPLETED | SADAM | 2
BAQER MOHEBI | WAREHOUSE | DXB | CHILLER NOT WORKING | NOT ATTENDED | (blank) | 2
BAQER MOHEBI | WAREHOUSE | DXB | NEED TO CHECK ALARM SYSTEM CH NO 6 | ATTENDED | MOHAMMED | 3
BAQER MOHEBI | WAREHOUSE | DXB | NEED TO CHECK ALARM SYSTEM CH NO 3 | COMPLETED | MOHAMMED | 3
BAQER MOHEBI | WAREHOUSE | DXB | NEED TO CHECK ALARM SYSTEM CH NO 5 | ATTENDED | MOHAMMED | 3
CAREEM | AL BARSHA | DXB | PPM Q3 | COMPLETED | GOVIND | 37
CAREEM | AL QUOZ | DXB | DOOR LIMIT SWITCH DAMAGE | COMPLETED | SADAM | 1
CAREEM | AL QUOZ | DXB | FREEZER COLD ROOM HIGH TEMP | COMPLETED | MOHAMMED | 1
CAREEM | AL RAFFA | DXB | CHILLER DOOR FRAME BROKEN | ATTENDED | MOHAMMED | 2
CAREEM | AL RAFFA | DXB | CHILLER DOOR FRAME BROKEN | ATTENDED | (blank) | 2
CAREEM | AL RAHA | AUH | PPM Q3 | COMPLETED | OLIVER | 37
CAREEM | AL RAHA | AUH | DOOR NOT CLOSING | COMPLETED | TROVEE | 1
CAREEM | AL RAWDAH | AUH | PPM Q3 | COMPLETED | OLIVER | 37
CAREEM | AL SAFA | DXB | CHILLER HIGH TEMP. | ATTENDED | SADAM | 2
CAREEM | AL SAFA | DXB | CHILLER HIGH TEMP. | COMPLETED | MUTHUKUMAR | 2
CAREEM | AL SAFA | DXB | PPM Q3 | COMPLETED | SUDHEESH | 37
CAREEM | AL SAFA | DXB | CHECK DOOR GASKET | COMPLETED | SHABEEB | 1
CAREEM | AL WASAL | DXB | COLD ROOM UNIT MOISTURE ISSUE | ATTENDED | SADAM | 1
CAREEM | ARABIAN CENTER | DXB | COLD ROOM FREEZER HIGH TEMP NOT ABOVE THAN -14 | COMPLETED | AHSAN | 1
CAREEM | ARJAN | DXB | CHILLER TEMP ISSUE. | COMPLETED | SADAM | 1
CAREEM | ARJAN | DXB | FREEZER TEMP. ISSUE | COMPLETED | SADAM | 1
CAREEM | ARJAN | DXB | PPM Q3 | COMPLETED | SUDHEESH | 37
CAREEM | BANIYAS | AUH | FREEZER COLD ROOM HIGH TEMP | COMPLETED | OLIVER | 1
CAREEM | BANIYAS | AUH | WATER PUMP LEAK | COMPLETED | RANDOLPH | 1
CAREEM | BANIYAS | DXB | WATER IN THE COLD ROOM PUMP | COMPLETED | OLIVER | 2
CAREEM | BANIYAS | DXB | WATER IN THE COLD ROOM PUMP | COMPLETED | RANDOLPH | 2
CAREEM | BB1 | DXB | PPM Q3 | COMPLETED | ABID, AJMEER | 37
CAREEM | BB2 | DXB | FREEZER CABINET NOT WORKING PROPERLY | COMPLETED | SHAFI | 1
CAREEM | BB2 | DXB | PPM Q3 | COMPLETED | GOVIND | 74
CAREEM | BB2 | DXB | FREEZER HIGHT TEMP. | COMPLETED | SHABEEB | 1
CAREEM | BB3 | DXB | MOISTURE ISSUE | COMPLETED | MOHAMMED | 2
CAREEM | BB3 | (blank) | MOISTURE ISSUE | ATTENDED | MOHAMMED | 2
CAREEM | CITY LAND | DXB | WATER LEAK IN DRAIN PUMP | ATTENDED | MUTHUKUMAR | 1
CAREEM | CITY LAND | DXB | DRAIN PUMP WATER LEAKGE | COMPLETED | SARAVANAN | 0
CAREEM | CITY LAND | DXB | FREEZER HIGHT TEMP. | COMPLETED | SADAM | 1
CAREEM | CITYLAND | DXB | COLD ROOM WATER PIMP MOISTURE ISSUE | COMPLETED | SADAM | 1
CAREEM | CITYLAND | DXB | COLD ROOM DOOR LOCK INSIDE CAP MISSING | COMPLETED | MOHAMMED | 1
CAREEM | DFC | DXB | PPM Q3 | COMPLETED | ZALAUDDIN | 37
CAREEM | DFC | DXB | EGG CHILLER DOOR ISSUE. | ATTENDED | SADAM | 1
CAREEM | DIC | DXB | CONDENSATE PUMP WATER SWEATING ISSUE | COMPLETED | MOHAMMED | 1
CAREEM | DIERA | DXB | CHILLER CHILLER COLD ROOM HIGH TEMP | COMPLETED | SARAVANAN | 1
CAREEM | DIERA | DXB | FREEZER COLD ROOM HIGH TEMP | COMPLETED | SHAFI | 1
CAREEM | DSO | DXB | FREEZER GLASS DOOR ISSUE | ATTENDED | SARAVANAN | 2
CAREEM | DSO | DXB | FREEZER GLASS DOOR ISSUE | ATTENDED | (blank) | 2
CAREEM | DSO | DXB | PPM Q3 | COMPLETED | GOVIND | 37
CAREEM | DWTC | DXB | PPM Q3 | COMPLETED | GOVIND | 37
CAREEM | E& | AUH | PPM Q3 | COMPLETED | OLIVER | 37
CAREEM | JADHAF | DXB | CHILLER CURTAIN ARE LOOSE | COMPLETED | SARAVANAN | 1
CAREEM | JLT | DXB | CHEST FREEZER NOT WORKING / FREEZER NO#6 HIGH TEMP ISSUE | ATTENDED | MOHAMMED | 2
CAREEM | JLT | DXB | F&V OPEN CHILLER OT WORKING | COMPLETED | SADAM | 1
CAREEM | JLT | DXB | FREEZER NO. 06 HIGH TEMP . | COMPLETED | SADAM | 2
CAREEM | JLT | DXB | FREEZER TEMP ISSUE | COMPLETED | SARAVANAN | 1
CAREEM | JLT | DXB | FREEZER TEMP. ISSUE | ATTENDED | SARAVANAN | 1
CAREEM | JVC LUNA | DXB | PPM Q3 | COMPLETED | ZALAUDDIN | 37
CAREEM | JVC PLAZA | DXB | CHILLER SLIDING DOOR ISSUE | ATTENDED | MOHAMMED | 1
CAREEM | JVC PLAZA | DXB | FREEZER TEMP.ISSUE | COMPLETED | SARAVANAN | 1
CAREEM | JVC PLAZA | DXB | PPM Q3 | COMPLETED | ABID, AJMEER | 37
CAREEM | JVT | DXB | FREEZER COLD ROOM NOT WORKING | COMPLETED | SADAM | 2
CAREEM | JVT | DXB | FREEZER COLD ROOM NOT WORKING | COMPLETED | VIGNESH/MOHAMMED | 2
CAREEM | JVT | DXB | FREEZER HIGH TEMP | COMPLETED | SARAVANAN | 1
CAREEM | JVT | DXB | INDOOR NEED TO SERVICE | (blank) | (blank) | 1
CAREEM | JVT | DXB | LEAK CHECK AND ARRESTING | COMPLETED | SHAFI | 1
CAREEM | JVT | DXB | Q 1 PPM FINISHED | COMPLETED | SADAM | 37
CAREEM | JVT | DXB | UNIT SERVICE | ATTENDED | SADAM | 2
CAREEM | JVT | DXB | UNIT SERVICE | COMPLETED | SADAM | 2
CAREEM | JVT | DXB | FREEZER COLD ROOM HIGH TEMP | COMPLETED | MOHAMMED | 1
CAREEM | MARINA | DXB | 2 CHILLER NOT WORKING | COMPLETED | SADAM | 1
CAREEM | MARINA | DXB | BRAKER TRIPING | COMPLETED | SARAVANAN | 3
CAREEM | MARINA | DXB | CHILLER SHUTDOWN | COMPLETED | MOHAMMED | 1
CAREEM | MARINA | DXB | OPEN CHILLER CHILLER TRIPPING ISSUE | ATTENDED | MOHAMMED | 1
CAREEM | MARINA | DXB | OPEN CHILLER NOT WORKING | ATTENDED | MOHAMMED | 3
CAREEM | MARINA | DXB | OPEN CHILLER NOT WORKING | COMPLETED | SADAM | 3
CAREEM | MARINA | DXB | PPM Q3 | COMPLETED | SUDHEESH | 74
CAREEM | MARINA | DXB | SOME DOOR STRIP LIGHT NOT WORKING | ATTENDED | SARAVANAN | 1
CAREEM | MARINA | DXB | LIGHT ISSUE | COMPLETED | SARVANAN | 0
CAREEM | MARINA | DXB | CHILLER NO.9 WATER ISSUE ,FREEZER NO.4 NOS LIGHT NOT WORKING | ATTENDED | SHABEEB | 1
CAREEM | MARINA | DXB | OPEN CHILLER SHUT DOWN | ATTENDED | SABITH ALI | 1
CAREEM | MARINA 1 | DXB | CHEST FREEZER NOT WORKING | COMPLETED | SADAM | 1
CAREEM | MEYDAN | DXB | WALKIN FREEZER CONDENSATE PUMP REPLACEMENT | COMPLETED | MOHAMMED | 2
CAREEM | MEYDAN | DXB | WALKIN FREEZER CONDENSATE PUMP WATER LEAK | COMPLETED | MOHAMMED | 2
CAREEM | MOTOR CITY | DXB | CHEST FREEZER NOT WORKING | ATTENDED | MOHAMMED | 1
CAREEM | MOTOR CITY | DXB | PPM | COMPLETED | ABID, AJMEER | 37
CAREEM | MOTOR CITY | DXB | CHILLER WATER LEAK AND DOOR ISSUE | ATTENDED | SADAM | 1
CAREEM | SHAMKHA | AUH | COLD ROOM NOT WORKING | COMPLETED | RANDOLPH | 1
CAREEM | STAR CITY | DXB | OUT DOOR ICE FORMATION | COMPLETED | SHAFI | 1
CAREEM | UMS | DXB | CHILELR DOORS NOT CLOSING PROPERLY | ATTENDED | SARAVANAN | 2
CAREEM | UMS | DXB | CHILELR DOORS NOT CLOSING PROPERLY | COMPLETED | SARAVANAN | 2
CAREEM | UMS | DXB | ICE CREAM FREEZER HIGH TEMP | COMPLETED | MOHAMMED | 2
CAREEM | UMS | DXB | ICE CREAM FREEZER HIGH TEMP | COMPLETED | SADAM | 2
CAREEM | UMS | DXB | PPM Q3 | COMPLETED | ABID, AJMEER | 37
CAREEM | UMS | DXB | TEMP.DISPLAY NOT SHOWING | COMPLETED | SARAVANAN | 1
CAREEM | WAREHOUSE JEBEL ALI | DXB | CHEST FREEZER TEMP. ISSUE | ATTENDED | SADAM | 1
CAREEM | JADAFF | AUH | COLD ROOM DOOR GASKET | COMPLETED | MOHAMMED | 2
CAREEM | JADAFF | DXB | COLD ROOM DOOR GASKET | ATTENDED | MOHAMMED | 2
CAREEM | ARABIAN STORE | DXB | DRAIN PUMP WATER LEAKGE | NOT ATTENDED | (blank) | 1
CAREEM | AL WASL | DXB | FREEZER COLD ROOM NOT WORKING | COMPLETED | AHSAN | 2
CAREEM | AL WASL | DXB | FREEZER COLD ROOM NOT WORKING | COMPLETED | SARVANAN | 2
CAREEM | AL WASL | DXB | NEED TO CLEAN PPM | NOT ATTENDED | (blank) | 1
CAREEM | DIC | DXB | PPM DONE DUBAI INTERNET CITY STORE | COMPLETED | ZALAUDIN | 1
ENOC | 32 | DXB | OPEN CHILLER IN PRONTO AREA | COMPLETED | SARAVANAN | 1
ENOC | 32 | (blank) | Open chiller in CStore 2 water leaking | NOT ATTENDED | (blank) | 1
ENOC | 66 | DXB | OPEN CHILLER NOT WORKING | COMPLETED | SHAFI | 0
ENOC | 95 | DXB | Bed freezer 04 tripping | ATTENDED | SADAM | 1
ENOC | 95 | DXB | OPEN CHILLER DOOR NO. 2 SHELVES RUSTY | ATTENDED | SARAVANAN | 4
ENOC | 95 | DXB | OPEN CHILLER NO 1 TRMP -5 | ATTENDED | MOHAMMED | 0
ENOC | 95 | (blank) | OPEN CHILLER WATER LEAKAG NO.4 | COMPLETED | SADAM | 0
ENOC | 305 | UMQ | CHILLER DOOR NOT CLOSING PROPERLY | ATTENDED | AHSAN | 2
ENOC | 305 | UMQ | CHILLER DOOR NOT CLOSING PROPERLY | COMPLETED | AHSAN | 2
ENOC | 305 | UMQ | FREEZER DRAIN LINE PIPE WATER LEAKING | ATTENDED | SABITH ALI | 2
ENOC | 305 | UMQ | FREEZER DRAIN LINE PIPE WATER LEAKING | COMPLETED | SABITH ALI | 2
ENOC | 401 | RAK | CHILLER CABINET DOOR NOT CLOSING AND GASKET DAMAGE | COMPLETED | SABITH ALI | 0
ENOC | 401 | RAK | GASKET ISSUE | COMPLETED | VIGNESH | 1
ENOC | 404 | RAK | DRINKS CHILLER DOOR GASKET | NOT ATTENDED | (blank) | 1
ENOC | 412 | DXB | VERTICAL FREEZER AND OPEN CHILLER INSPECTION | COMPLETED | SHAFI | 0
ENOC | 412 | RAK | OPEN CHILLER INSTALATION | ATTENDED | DENNIS | 0
ENOC | 412 | RAK | Spray painting of existing shelves insid | COMPLETED | SABITH ALI | 1
ENOC | 412 | RAK | TESTING,AND INSTALLATION OF THE VERTICA | COMPLETED | SHAFI | 4
ENOC | 412 | RAK | VERTICAL CHILLER BOTTOM COVER AND CABINET SHELF REPAINTING | ATTENDED | SABITH ALI | 1
ENOC | 412 | RAK | FREERER HIGH TEMP. AND CHILLER WATER LEAK | COMPLETED | RACEL | 0
ENOC | 412 | RAK | OPEN CHILLER WATER LEAKAG/CHENGEING CONTROLER | COMPLETED | RACEL | 2
ENOC | 412 | (blank) | OPEN CHILLER WATER LEAKAG | ATTENDED | AHSAN | 2
ENOC | 507 | FUJ | Door Chiller having unnecessary sound ne | COMPLETED | SABITH ALI | 1
ENOC | 508 | FUJ | CHILLER 1-5 DOWN COVER SHEET DETACHED | ATTENDED | VIGNESH | 2
ENOC | 508 | FUJ | CHILLER 1-5 DOWN COVER SHEET DETACHED | COMPLETED | VIGNESH | 2
ENOC | 508 | FUJ | OPEN CHILLER TRIPPING ISSUE | COMPLETED | VIGNESH | 4
ENOC | 509 | FUJ | ICE FORMATION ON CHILLER COMPRESSOR | COMPLETED | VIGNESH | 1
ENOC | 509 | FUJ | ice formation on walk in freezer door | ATTENDED | VIGNESH | 4
ENOC | 509 | FUJ | OPEN CHILLER LIGHT DETACHED | ATTENDED | AHSAN | 2
ENOC | 509 | FUJ | OPEN CHILLER LIGHT DETACHED | ATTENDED | TALIB | 2
ENOC | 509 | FUJ | OPEN CHILLER LIGHT NOT WORKING | ATTENDED | SABITH ALI | 3
ENOC | 509 | FUJ | PAINTING OF CHILELR AND FREEZER SUPPORT AND FRAME | COMPLETED | SABITH ALI | 0
ENOC | 509 | FUJ | REFIXING OF SHELVES | COMPLETED | BIJU | 0
ENOC | 509 | FUJ | W/C UNIT SHEET DAMAGE | COMPLETED | SABITH ALI | 1
ENOC | 509 | FUJ | WALKIN CHILLER AND FREEZER SHELVES REMOVE | COMPLETED | BIJU, LORIMER | 0
ENOC | 509 | FUJ | LIGHT CHANGE | COMPLETED | RACEL | 3
ENOC | 509 | (blank) | OPEN CHILLER LIGHT NOT WORKING | ATTENDED | SABITH ALI | 3
ENOC | 1005 | DXB | PPM | COMPLETED | BIJU | 1
ENOC | 1005 | DXB | WALK IN CHILLER HIHG TEMP. | COMPLETED | SABITH ALI | 1
ENOC | 1005 | DXB | walk-in chiller temperature not stable. | COMPLETED | SARAVANAN | 1
ENOC | 1005 | (blank) | Walk in chiller temperature very high | COMPLETED | SABITH ALI | 1
ENOC | 1007 | DXB | CHILLER LIGHT | ATTENDED | SARAVANAN | 2
ENOC | 1007 | DXB | CHILLER LIGHT | COMPLETED | SARAVANAN | 2
ENOC | 1007 | DXB | Open Chiller temperature high | ATTENDED | SHAFI | 1
ENOC | 1007 | DXB | PRONTO BED FREEZER NOT WORKING. | COMPLETED | RACEL | 1
ENOC | 1007 | DXB | WALKIN CHILLER DOOR#4 RUBBER LINING | COMPLETED | SADAM | 1
ENOC | 1009 | DXB | OPEN CHILLER NOT WORKING | COMPLETED | SHAFI | 0
ENOC | 1009 | DXB | WALK IN FREEZER ICE FORMATION | ATTENDED | SADAM | 4
ENOC | 1011 | DXB | OPEN CHILLER HIGH TEMP | COMPLETED | SADAM | 0
ENOC | 1011 | DXB | OPEN CHILLER NOT WORKING | ATTENDED | MOHAMMED | 0
ENOC | 1011 | DXB | PPM | COMPLETED | MUTHUKUMAR | 0
ENOC | 1011 | DXB | CALIBRATION REQUEST FOR CHILLER/FREEZER | NOT ATTENDED | (blank) | 1
ENOC | 1012 | DXB | Walk in chiller ceiling lights are buste | ATTENDED | SARAVANAN | 2
ENOC | 1012 | DXB | Walk in chiller ceiling lights are buste | COMPLETED | SARAVANAN | 2
ENOC | 1012 | DXB | WALK IN FREEZER TEMP. ISSUE | COMPLETED | SADAM | 0
ENOC | 1012 | DXB | Walk in freezer temperature is high | COMPLETED | SADAM | 1
ENOC | 1013 | DXB | OPEN CHILLER BOTTOM AREA IS TOO RUSTY | ATTENDED | SARAVANAN | 1
ENOC | 1013 | DXB | WALK IN CHILLER TEMPERATURE | COMPLETED | SHABEEB | 1
ENOC | 1016 | DXB | OPEN CHILLER LIGHT NOT WORKING | COMPLETED | MOHAMMED | 1
ENOC | 1017 | DXB | ABOVE THE OPEN CHILLER CABINET SHELF BOT | ATTENDED | SARAVANAN | 2
ENOC | 1017 | DXB | ABOVE THE OPEN CHILLER CABINET SHELF BOT | COMPLETED | SARAVANAN | 2
ENOC | 1019 | DXB | HALOGEN LIGHT NOT WORKING | ATTENDED | SADAM | 1
ENOC | 1019 | DXB | OPEN CHILLER NEED GLASS INSTALLATION | ATTENDED | SADAM | 0
ENOC | 1019 | DXB | WALKIN CHILLER LIGHT NOT WORKING | ATTENDED | SHAFI | 2
ENOC | 1019 | DXB | LIGHT CHANGE | COMPLETED | SABITH ALI | 2
ENOC | 1022 | DXB | FREEZER CURTAIN IS DAMAGED | ATTENDED | MOHAMMED | 6
ENOC | 1022 | DXB | NEED TO FIX PVC CURTAIN | COMPLETED | SARAVANAN | 3
ENOC | 1022 | DXB | WALK IN CHILLER WATER LEAKAGE ISSUE | COMPLETED | SARVANAN | 1
ENOC | 1022 | DXB | Ice formation inside freezer | NOT ATTENDED | (blank) | 1
ENOC | 1023 | DXB | Bed-freezer lights not working. | ATTENDED | SADAM | 2
ENOC | 1023 | DXB | Bed-freezer lights not working. | COMPLETED | SADAM | 2
ENOC | 1027 | DXB | DOOE GASKET DAMAGE CHILLER | ATTENDED | SARAVANAN | 1
ENOC | 1027 | DXB | OPEN CHILLER NOISE ISSUE | COMPLETED | SADAM | 1
ENOC | 1027 | DXB | Q 4 PPM | COMPLETED | MUTHUKUMAR | 37
ENOC | 1027 | DXB | WALKIN CHILLER DOOR TOUCHING | ATTENDED | SHAFI, DENNIS | 2
ENOC | 1027 | DXB | WALKIN CHILLER DOOR TOUCHING | COMPLETED | SHAFI, DENNIS | 2
ENOC | 1027 | DXB | WALKIN FREEZER NOT COOLING | ATTENDED | SARAVANAN | 1
ENOC | 1027 | DXB | ICE IS BUILDING UP ON DISPLAY PRODUCTS I | ATTENDED | SARAVANAN | 2
ENOC | 1027 | ENOC | WALKIN FREEZER DOOR NOT CLOSING | COMPLETED | SARAVANAN | 1
ENOC | 1029 | DXB | PPM | COMPLETED | MUTHUKUMAR | 0
ENOC | 1029 | DXB | PRONTO VERTICAL CHILLER | COMPLETED | SARAVANAN | 1
ENOC | 1029 | DXB | Store refrigeration required PM | NOT ATTENDED | (blank) | 1
ENOC | 1031 | DXB | CHILLER WATER LEAK | COMPLETED | SARAVANAN | 2
ENOC | 1031 | DXB | walk in chiller door cannot close | COMPLETED | SHAFI | 2
ENOC | 1031 | DXB | chiller pipe is leaking | COMPLETED | (blank) | 2
ENOC | 1031 | (blank) | walk in chiller door cannot close | ATTENDED | (blank) | 2
ENOC | 1032 | DXB | WALK IN FREEZER ICE FORMATION | ATTENDED | SARVANAN | 2
ENOC | 1032 | DXB | WALKIN FREEZER ICE FORMATION | COMPLETED | MOHAMMED | 1
ENOC | 1032 | (blank) | OPEN CHILLER SHELF FOR REPAINTING | COMPLETED | SARAVANAN | 1
ENOC | 1032 | (blank) | WALK IN FREEZER ICE FORMATION | NOT ATTENDED | (blank) | 2
ENOC | 1032 | (blank) | WALK-IN FREEZER | COMPLETED | SABITH ALI | 1
ENOC | 1033 | DXB | PPM | COMPLETED | BIJU,MUTHUKUMAR | 0
ENOC | 1033 | DXB | WALK IN FREEZER ICE FORMATION | COMPLETED | SARAVANAN | 2
ENOC | 1033 | DXB | WALKIN FREEZER GASKET NEED TO CHECK AND ICE FORMATION | COMPLETED | SHAFI | 0
ENOC | 1033 | DXB | WALKIN FREEZER ICE - GASKET INSTALLATION | COMPLETED | SADAM | 2
ENOC | 1033 | DXB | WALKIN FREEZER ICE FORMATION | COMPLETED | SHAFI | 2
ENOC | 1033 | (blank) | WALK IN FREEZER ICE FORMATION | ATTENDED | SADAM | 2
ENOC | 1035 | DXB | DRAIN PIPE LINE IN WALKIN CHILLER | ATTENDED | SABITH ALI | 2
ENOC | 1035 | DXB | DRAIN PIPE LINE IN WALKIN CHILLER | COMPLETED | SABITH ALI | 2
ENOC | 1035 | DXB | WALK-IN CHILLER DOOR NOT CLOSING | ATTENDED | SHAFI | 2
ENOC | 1035 | DXB | WALK-IN CHILLER DOOR NOT CLOSING | COMPLETED | SHAFI | 2
ENOC | 1035 | DXB | CHILLER AND FREEZER ISSUES | ATTENDED | MOHAMMED | 0
ENOC | 1035 | DXB | Walk in freezer not working | COMPLETED | SARVANAN | 1
ENOC | 1036 | DXB | OPEN CHILLER SHELVES RUSTED | ATTENDED | SADAM | 1
ENOC | 1036 | DXB | WALKIN FREEZER INSULATION DAMAGE | COMPLETED | BIJU | 0
ENOC | 1036 | DXB | WALK IN FREEZER TEMP.ISSUE | ATTENDED | SADAM | 0
ENOC | 1036 | DXB | Walk-in chiller gasket and door rubber | NOT ATTENDED | (blank) | 1
ENOC | 1036 | DXB | Walk in freezer not working | ATTENDED | SADAM | 0
ENOC | 1039 | DXB | ICE FORMATION IN WALKIN FREEZER | COMPLETED | SADAM | 1
ENOC | 1039 | DXB | ICE FORMING IN WALK IN FREEZER | ATTENDED | MOHAMMED | 2
ENOC | 1039 | DXB | ICE FORMING IN WALK IN FREEZER | COMPLETED | MOHAMMED | 2
ENOC | 1039 | DXB | PPM | COMPLETED | MUTHUKUMAR | 0
ENOC | 1039 | DXB | ICE FORMATION IN VERTICLE FREEZER | COMPLETED | SARVANAN | 0
ENOC | 1039 | (blank) | chiller door not closing properly. | COMPLETED | SADAM | 1
ENOC | 1039 | (blank) | Ice formation in walk in freezer | ATTENDED | SADAM | 1
ENOC | 1039 | (blank) | Sandwich chiller having noise | COMPLETED | SADAM | 1
ENOC | 1041 | DXB | OPEN CHILLER HIGH TEMP | COMPLETED | SHAFI | 0
ENOC | 1041 | DXB | Walk in chiller bulb light 4 nos. busted | ATTENDED | SARAVANAN | 4
ENOC | 1041 | DXB | WALKIN CHILLER INSIDE LIGHT BUSTED | COMPLETED | RAJESH | 1
ENOC | 1041 | DXB | walk in chiller door rubber damaged need | ATTENDED | MOHAMMED | 2
ENOC | 1041 | DXB | walk in chiller door rubber damaged need | NOT ATTENDED | (blank) | 2
ENOC | 1041 | DXB | chiller shelf rusty need to change | ATTENDED | MOHAMMED | 2
ENOC | 1041 | DXB | chiller shelf rusty need to change | NOT ATTENDED | (blank) | 2
ENOC | 1042 | DXB | Q 4 PPM | COMPLETED | MUTHUKUMAR | 37
ENOC | 1042 | DXB | WALKIN FREEZER | COMPLETED | MOHAMMED | 1
ENOC | 1042 | DXB | pronto chillier door | COMPLETED | MUSTAFA | 1
ENOC | 1045 | DXB | Q 4 PPM | COMPLETED | BIJU | 37
ENOC | 1045 | RAK | VERTICAL GFREEZER TRIPPING | COMPLETED | SHAFI | 0
ENOC | 1052 | DXB | bed freezer showing -14 temp | ATTENDED | SARAVANAN | 1
ENOC | 1052 | DXB | GASKET FOR WALKIN FREEZER DOOR, DAMAGE | ATTENDED | SHAFI | 2
ENOC | 1052 | DXB | GASKET FOR WALKIN FREEZER DOOR, DAMAGE | COMPLETED | SHAFI | 2
ENOC | 1052 | DXB | UINSULATION OF DIGITAL THERMOMETER IN OPEN CHILLER CABINET | COMPLETED | SABITH ALI | 0
ENOC | 1052 | DXB | open chiller showing high temp 10.1 | COMPLETED | MOHAMMED | 1
ENOC | 1054 | DXB | ICE FORMATION IN WALKIN FREEZER | COMPLETED | RACEL | 2
ENOC | 1055 | DXB | PRONTO AMBIENT DISPLAY CHILLER NOT WORKING | COMPLETED | MOHAMMED | 0
ENOC | 1055 | DXB | WALKIN CHILLER HIGH TEMP | COMPLETED | SADAM | 0
ENOC | 1055 | DXB | Walk in chiller temperature fluctuating | NOT ATTENDED | (blank) | 1
ENOC | 1056 | DXB | PPM | COMPLETED | SANOJ | 0
ENOC | 1056 | DXB | vertical freezer 1 light busted | ATTENDED | SARAVANAN | 2
ENOC | 1056 | DXB | vertical freezer 1 light busted | ATTENDED | SHABEEB | 2
ENOC | 1056 | DXB | vertical freezer 1 light busted | ATTENDED | (blank) | 2
ENOC | 1056 | DXB | vertical freezer 1 light busted | COMPLETED | SARAVANAN | 2
ENOC | 1056 | DXB | WALKIN FREEZER LIGHT ISSUE | COMPLETED | SHABEEB | 0
ENOC | 1057 | DXB | BED FREEZER TEMP. READER IS DETACHED | ATTENDED | SADAM | 1
ENOC | 1057 | DXB | SUPPLY OF COLD ROOM DOOR HINGES FOR WALKIN | ATTENDED | SADAM | 2
ENOC | 1057 | DXB | SUPPLY OF COLD ROOM DOOR HINGES FOR WALKIN | COMPLETED | SADAM | 2
ENOC | 1057 | DXB | VERTICAL FREEZER ICE FORMATION | ATTENDED | SADAM | 2
ENOC | 1057 | DXB | Chiller Door 1 to 10 1 no. light is bust | NOT ATTENDED | (blank) | 1
ENOC | 1057 | DXB | WALKIN CHILLER NOT WORKING | COMPLETED | SADAM | 0
ENOC | 1057 | DXB | walk in chiller temp is breakdown | COMPLETED | MOHAMMED | 2
ENOC | 1057 | DXB | walk in chiller temp is breakdown | NOT ATTENDED | (blank) | 2
ENOC | 1060 | DXB | BED FREEZER NOT WORKING | ATTENDED | SADAM | 0
ENOC | 1060 | DXB | BED FREEZER NOT WORKING | ATTENDED | SHABEEB | 1
ENOC | 1060 | DXB | BED FREEZER NOT WORKING | COMPLETED | SHABEEB | 0
ENOC | 1060 | (blank) | London Diary freezer 1 is not working | NOT ATTENDED | (blank) | 1
ENOC | 1060 | (blank) | BED FREEZER NOT WORKING | COMPLETED | SADAM | 1
ENOC | 1061 | (blank) | vertical freezer metal plate need fix | ATTENDED | (blank) | 2
ENOC | 1061 | (blank) | vertical freezer metal plate need fix | COMPLETED | SHAFI | 2
ENOC | 1062 | DXB | BED FREEZER NOT WORKING | COMPLETED | MOHAMMED | 0
ENOC | 1062 | DXB | PPM | COMPLETED | BIJU | 1
ENOC | 1062 | DXB | PRONTO FREEZER NOT WORKING | COMPLETED | SHAFI | 1
ENOC | 1062 | DXB | PRONTO VERTICAL CHILLER | COMPLETED | SHAFI | 1
ENOC | 1063 | DXB | BED FREEZER GASKET | COMPLETED | MUSTAFA | 0
ENOC | 1063 | DXB | BED FREEZER INSULATION CHANGE | COMPLETED | (blank) | 0
ENOC | 1063 | DXB | BED FREEZER SHUTDOWN | COMPLETED | MOHAMMED | 0
ENOC | 1063 | DXB | PPM | COMPLETED | MUTHUKUMAR | 1
ENOC | 1063 | DXB | Pronto display chiller air filter | NOT ATTENDED | (blank) | 1
ENOC | 1071 | DXB | Walk in chiller is not working properly | COMPLETED | SADAM | 1
ENOC | 1071 | DXB | WALKIN CHILLER DOOR HANDEL FIXING | COMPLETED | SHAFI | 0
ENOC | 1072 | DXB | OPEN CHILLER WATER DRAINAGE REPAINT | COMPLETED | SHAFI | 1
ENOC | 1072 | DXB | WALKIN FREEZER CURTAIN DAMAGED | COMPLETED | SHAFI | 1
ENOC | 1072 | DXB | Wall in the counter area need to repaint | COMPLETED | SHAFI | 1
ENOC | 1074 | DXB | BED FREEZER CREATE ICE FORMATION | ATTENDED | SADAM | 1
ENOC | 1074 | DXB | VERTICAL FREEZER NOT WORKING | COMPLETED | SARAVANAN | 1
ENOC | 1074 | DXB | WALKIN FREEZER 2 DOOR NOT COOLING AUTOMATICALLY. REPLACEMENT OF NEW SPRING TENSION SET, NEW GASKET WITH NEW PLASTIC HOLDER | COMPLETED | DENNIS, SHAFI | 0
ENOC | 1074 | DXB | WALKIN FREEZER HIGH TEMP AND DEFROST TIMING ISSUE | COMPLETED | SHAFI | 0
ENOC | 1074 | DXB | WALK IN FREEZER DOOR ICE FORMATION | COMPLETED | SARVANAN | 1
ENOC | 1074 | DXB | WALKIN FREEZER DOOR ISUUE, CANT OPEN | ATTENDED | SADAM | 0
ENOC | 1074 | DXB | Walk in freezer door hard to open | COMPLETED | MUSTAFA | 1
ENOC | 1074 | (blank) | Condenser Cleaning/Refrigeration PM | NOT ATTENDED | (blank) | 1
ENOC | 1079 | DXB | Bed freezer top glass | NOT ATTENDED | SHABAN | 1
ENOC | 1079 | DXB | CHILLER DOOR HANDLE BROKEN | ATTENDED | SARAVANAN | 2
ENOC | 1079 | DXB | CHILLER DOOR HANDLE BROKEN | COMPLETED | SARAVANAN | 2
ENOC | 1079 | DXB | DELI CHILLER 1 BLOCKED DRAINAGE | ATTENDED | SADAM | 2
ENOC | 1079 | DXB | DELI CHILLER 1 BLOCKED DRAINAGE | COMPLETED | SADAM | 2
ENOC | 1079 | DXB | FOOD BENCH CHILLER DOOR HANDLE | ATTENDED | SARAVANAN | 2
ENOC | 1079 | DXB | FOOD BENCH CHILLER DOOR HANDLE | COMPLETED | SARAVANAN | 2
ENOC | 1079 | DXB | ICE FORMATION IN WALKIN FREEZER | ATTENDED | SARAVANAN | 2
ENOC | 1079 | DXB | ICE FORMATION IN WALKIN FREEZER | COMPLETED | SARAVANAN | 2
ENOC | 1079 | DXB | NOISY SOUND FROM FOOD BENCH FREEZER | ATTENDED | SARAVANAN | 2
ENOC | 1079 | DXB | NOISY SOUND FROM FOOD BENCH FREEZER | COMPLETED | SARAVANAN | 2
ENOC | 1079 | DXB | PLASTIC CURTAIN IN WALKIN CHILLER | ATTENDED | SADAM | 4
ENOC | 1079 | DXB | PPM | COMPLETED | BIJU | 0
ENOC | 1079 | DXB | WALKIN CHILLER PLASTIC CURTAIN | COMPLETED | SARAVANAN | 1
ENOC | 1079 | DXB | Deli Counter Chiller light is not working | NOT ATTENDED | (blank) | 1
ENOC | 1079 | (blank) | Rubber gasket | ATTENDED | SARAVANAN | 1
ENOC | 1080 | DXB | METAL SHEET UNDER THE OPEN CHILLER | COMPLETED | SADAM | 1
ENOC | 1080 | DXB | Walk in chiller fan not working /rusty | ATTENDED | SADAM | 2
ENOC | 1080 | DXB | Walk in chiller fan not working /rusty | COMPLETED | SADAM | 2
ENOC | 1080 | DXB | WALKIN FREEZER ICE FORMATION | ATTENDED | MOHAMMED | 1
ENOC | 1080 | DXB | WALKIN FREEZER ICE FORMATION AND RUSTY | COMPLETED | SADAM | 1
ENOC | 1080 | DXB | Walk-in Freezer main drainage is clogged | COMPLETED | SADAM | 1
ENOC | 1080 | DXB | WALKIN FREEZER TEMP ISSUE -17 | ATTENDED | SHAFI | 1
ENOC | 1080 | DXB | WATER Leaking under OPEN CHILLER | COMPLETED | SADAM | 1
ENOC | 1080 | DXB | WATER LEAKAGE IN CHILLER | COMPLETED | SADAM | 1
ENOC | 1080 | DXB | VERTICALE FREEZER ISSUE | COMPLETED | SARVANAN | 0
ENOC | 1081 | DXB | pronto display chiller not working | ATTENDED | SARAVANAN | 1
ENOC | 1081 | DXB | WALKIN FREEZER DUST WAS FALLING IN ITEMS | ATTENDED | SHAFI | 1
ENOC | 1081 | DXB | WALK IN CHILLER HIGH TEMP | COMPLETED | SARVANAN | 1
ENOC | 1085 | DXB | VERTICAL FREEZER NEED TO CHECK | COMPLETED | SADAM | 2
ENOC | 1085 | DXB | VERTICAL FREEZER NEED TO CHECK | COMPLETED | SHAFI | 2
ENOC | 1085 | DXB | Walk in chiller plastic curtain is damag | ATTENDED | SARAVANAN | 6
ENOC | 1085 | DXB | WALKIN CHILLER PVC CURTIN FIXING | COMPLETED | SARAVANAN | 3
ENOC | 1086 | DXB | VERTICAL FREEZER NOT WORKING | COMPLETED | SARVANAN | 1
ENOC | 1086 | DXB | WALKIN CHILLER HIGH TEMP | ATTENDED | MOHAMMED | 1
ENOC | 1086 | DXB | WALKIN CHILLER HIGH TEMP | COMPLETED | SADAM | 0
ENOC | 1086 | ENOC | WALKIN CHILLER NOT WORKING | COMPLETED | MOHAMMED | 1
ENOC | 1088 | DXB | WALKIN FREEZER DOOR GASKET | ATTENDED | SHAFI | 2
ENOC | 1088 | DXB | WALKIN FREEZER DOOR GASKET | COMPLETED | SHAFI | 2
ENOC | 1088 | DXB | Walking freezer ice formation | ATTENDED | SADAM | 4
ENOC | 1088 | DXB | WALKIN FREEZER NO GAS KET | ATTENDED | SARVANAN | 1
ENOC | 1092 | DXB | OPEN CHILLER HIGH TEMP | COMPLETED | MOHAMMED | 0
ENOC | 1092 | DXB | PPM | COMPLETED | MUTHUKUMAR | 0
ENOC | 1092 | DXB | PVC CURTAIN REPLACEMENT | ATTENDED | MOHAMMED | 2
ENOC | 1092 | DXB | PVC CURTAIN REPLACEMENT | COMPLETED | MOHAMMED | 2
ENOC | 1094 | DXB | PRONTO FREEZER TEMP SHOWING -0.4 | COMPLETED | SADAM | 1
ENOC | 1094 | DXB | WALKIN FREEZER HIGH TEMP | COMPLETED | VIGNESH | 0
ENOC | 1094 | DXB | walk in freezer ice formation in condens | COMPLETED | SADAM | 1
ENOC | 1099 | DXB | PPM | COMPLETED | BIJU | 0
ENOC | 1099 | DXB | Vertical Chiller for Flower | ATTENDED | SARAVANAN | 4
ENOC | 1099 | DXB | WALKIN FREEZER BREAKDOWN | ATTENDED | SARAVANAN | 1
ENOC | 1099 | DXB | WALKIN FREEZER HIGH TEMP | COMPLETED | SARAVANAN | 0
ENOC | 1099 | DXB | WALKIN FREEZER HIGH TEMP | COMPLETED | SABITH ALI | 0
ENOC | 1099 | DXB | WALKIN FREEZER SHUTDOWN | COMPLETED | SHAFI | 0
ENOC | 1099 | DXB | C-store Chiller Display Shelves Repaint | ATTENDED | BIJU | 2
ENOC | 1099 | DXB | C-store Chiller Display Shelves Repaint | NOT ATTENDED | (blank) | 2
ENOC | 1101 | SHJ | DIGITAL THERMOMETER INSTALLATION | COMPLETED | SABITH ALI | 0
ENOC | 1103 | SHJ | WALKIN CHILLER DOOR GASKET DAMAGED | COMPLETED | SABITH ALI | 1
ENOC | 1103 | SHJ | WALK IN CHILLER GASKIT DAMAGE | ATTENDED | AHSAN | 2
ENOC | 1117 | SHJ | FREEZER TEMP ISSUE | COMPLETED | SELVAN | 1
ENOC | 1125 | SHJ | OPEN CHILLER HIGH TEMP | ATTENDED | AHSAN | 4
ENOC | 1125 | SHJ | OPEN CHILLER TEMP ISSUE | COMPLETED | VIGNESH | 0
ENOC | 1125 | SHJ | VERTICAL FREEZER HGH TEMP. | COMPLETED | AHSAN | 2
ENOC | 1125 | (blank) | Walk in freezer not working. | COMPLETED | VIGNESH | 1
ENOC | 1126 | SHJ | COMPRESSOR NRRD TO BE CHNGE | COMPLETED | AHSAN | 1
ENOC | 1126 | SHJ | OPEN CHILLER NOT WORKING PROPERLY | ATTENDED | RACEL | 1
ENOC | 1126 | SHJ | VERTICAL FREEZER HGH TEMP. | ATTENDED | RACEL | 2
ENOC | 1126 | (blank) | VERTICAL FREEZER NOT WORKING | COMPLETED | VIGNESH | 1
ENOC | 1127 | SHJ | OPEN CHILLER - CONTROLLER REPLACEMENT | COMPLETED | VIGNESH | 0
ENOC | 1127 | SHJ | OPEN CHILLER HIGH TEMP | ATTENDED | AHSAN | 0
ENOC | 1127 | SHJ | WALKIN CHILLER HIGH TEMP | COMPLETED | AHSAN | 1
ENOC | 1135 | SHJ | BED FREEZER TEMP. | COMPLETED | AHSAN | 1
ENOC | 1135 | SHJ | ICE CREAM BED FREEZER NOT WORKING | COMPLETED | VIGNESH | 1
ENOC | 1138 | SHJ | OPEN CHILLER WATER LEAK | COMPLETED | VIGNESH | 1
ENOC | 1142 | SHJ | FREEZER COLD ROOM WATER LEAK | ATTENDED | AHSAN | 2
ENOC | 1142 | SHJ | FREEZER COLD ROOM WATER LEAK | COMPLETED | RACEL | 2
ENOC | 1142 | SHJ | VERTICAL FREEZER TEMP. ISSUE | COMPLETED | RACEL | 0
ENOC | 1142 | SHJ | WALKIN FREEZER WATER LEAK | COMPLETED | RACEL | 0
ENOC | 1142 | SHJ | WALKIN FREEZER WATER LEKA AND ICE FORMATION | ATTENDED | VIGNESH | 1
ENOC | 1142 | SHJ | WATER DRIPPING IN WALK IN FREEZER | ATTENDED | VIGNESH | 1
ENOC | 1161 | SHJ | PRONTO FREEZER TEMP ISSUE. | COMPLETED | SABITH ALI | 0
ENOC | 1161 | SHJ | PRONTO VERTICAL FREEZER HIGH TEMP. | COMPLETED | AHSAN | 0
ENOC | 1179 | SHJ | REPLACEMNET OF LED LIGHT FOR FREEZER | COMPLETED | VIGNESH | 1
ENOC | 1204 | AJM | tube Light Inside Freezer Not working | COMPLETED | RACEL | 1
ENOC | 1204 | DXB | OPEN CHILLER TEMP ISSUE | NOT ATTENDED | (blank) | 0
ENOC | 1205 | AJM | BACKUP FREEZER HAVE ICE FORMATION | ATTENDED | RACEL | 1
ENOC | 1205 | AJM | CHILLER GOING ON -VE TEMP | COMPLETED | VIGNESH | 0
ENOC | 1205 | AJM | CHILLER TEMP SHOWING NEGATIVE, NO COOLING | COMPLETED | RACEL | 0
ENOC | 1205 | AJM | OPEN CHILLER CONTINOUSLY IN DEF MODE | COMPLETED | AHSAN | 1
ENOC | 1205 | AJM | OPEN CHILLER NOT WORKING | COMPLETED | AHSAN | 1
ENOC | 1205 | AJM | WALKIN FREEZER ICE FORMATION IN FLOOR | COMPLETED | AHSAN | 1
ENOC | 1205 | DXB | WALK IN FREEZER ICE FORMATION | COMPLETED | VIGNESH | 4
ENOC | 1205 | DXB | lights (walk in chiller) | NOT ATTENDED | (blank) | 2
ENOC | 1205 | SHJ | WALK IN CHILLER LIGHT NOT WORKING | COMPLETED | RACEL | 2
ENOC | 1205 | SHJ | DOOR BTTOM SIDE GASKET DAMAGE IN WALK IN FREEZER &LIGHT NOT WORKING | COMPLETED | RACEL | 0
ENOC | 1239 | AJM | INSIDE WALKIN CHILLER LIGHT NOT WORKING | ATTENDED | (blank) | 2
ENOC | 1239 | AJM | INSIDE WALKIN CHILLER LIGHT NOT WORKING | COMPLETED | RACEL | 2
ENOC | 1401 | DXB | OLD FREEZER NEED TO REPAIR | COMPLETED | SARAVANAN | 1
ENOC | 1401 | RAK | deli chiller need to check for sandwich | ATTENDED | SABITH ALI | 1
ENOC | 1401 | RAK | SKOPE VERTICAL CHILLER UNIT NEED TO CHACK AND CONDITION REPORT | COMPLETED | VIGNESH | 1
ENOC | 1401 | RAK | WALKIN CHILLER NOISE ISSUE | COMPLETED | VIGNESH | 0
ENOC | 1401 | RAK | WALKIN CHILLER NOISE ISSUE | COMPLETED | SABITH ALI | 0
ENOC | 1401 | RAK | WALKIN FREEZER SHOUT DOWN | COMPLETED | SABITH ALI | 0
ENOC | 1401 | (blank) | WALKIN FREEZER SHOUT DOWN | COMPLETED | SABITH ALI | 0
ENOC | 1444 | RAK | DOOR FRAME FALL DOWN | COMPLETED | SABITH ALI | 2
ENOC | 1444 | RAK | Water droppings walk-in chiller ceiling. | COMPLETED | RACEL | 1
ENOC | 1444 | (blank) | CHILLER LIGHT HOLDER DAMAGE | ATTENDED | (blank) | 2
ENOC | 1511 | FUJ | 1 BUSTED LIGHTED LIGHT IN PRONTO DISPLAY | ATTENDED | SABITH ALI | 6
ENOC | 1511 | FUJ | 1 BUSTED LIGHTED LIGHT IN PRONTO DISPLAY | COMPLETED | VIGNESH | 3
ENOC | 1511 | SHJ | PRONTO VERTICAL FREEZER IS NOT WORKING | ATTENDED | RACEL | 1
ENOC | 1511 | SHJ | REPLACE COMPRESSOR | COMPLETED | RACEL | 0
ENOC | 1606 | DXB | DISPLAY CHILLER DOOR NEED TO FIX | NOT ATTENDED | (blank) | 1
ENOC | 1634 | DXB | WALKIN CHILLER HIGH TEMP | COMPLETED | MOHAMMED | 0
ENOC | 1634 | DXB | WALK IN CHILLER ICE FORMATION | COMPLETED | SADAM | 2
ENOC | 1634 | DXB | WALK IN CHILLER ICE FORMATION | NOT ATTENDED | (blank) | 2
ENOC | 1634 | DXB | TEMP ISSUE. WALK IN CHILLER | COMPLETED | MOHAMMED | 0
ENOC | 2020 | DXB | BED FREEZER LIGHT NOT WORKING | ATTENDED | SARAVANAN | 2
ENOC | 2020 | DXB | BED FREEZER LIGHT NOT WORKING | COMPLETED | SARAVANAN | 2
ENOC | 2020 | DXB | PPM | COMPLETED | MUTHUKUMAR | 1
ENOC | 2020 | DXB | VERTICAL FREEZER TEMP NOT WORKING | COMPLETED | SADAM | 1
ENOC | 2020 | DXB | Pronto walk in freezer | COMPLETED | SADAM | 1
ENOC | 4002 | DXB | WATER LEAK FROM CHILLER#2 | ATTENDED | SABITH ALI | 3
ENOC | 4002 | DXB | WATER LEAKAGE FROM CHILLER 2 | COMPLETED | SABITH ALI | 1
ENOC | 4007 | DXB | CHILLER #1 LIGHT NOT WORKING AND HIGH TEMP | COMPLETED | SARAVANAN | 1
ENOC | 4007 | DXB | CHILLER #2 | ATTENDED | SARAVANAN | 4
ENOC | 4009 | DXB | CHILLER WATER LEAK | ATTENDED | SABITH ALI | 0
ENOC | 4009 | DXB | CHILLER WATER LEAK | COMPLETED | SABITH ALI | 0
ENOC | 4009 | DXB | WATER LEAKAGE | COMPLETED | SABITH ALI | 1
ENOC | 4016 | DXB | 2 ND CHILLER NOT WORKING | ATTENDED | SARAVANAN | 2
ENOC | 4016 | DXB | 2 ND CHILLER NOT WORKING | COMPLETED | SARAVANAN | 2
ENOC | 4016 | DXB | REPLACEMENT OF COMPRESSOR OF CHILLER#3 | COMPLETED | SABITH ALI | 0
ENOC | 4016 | DXB | WATER LEAK FROM OPEN CHILLER | COMPLETED | SARAVANAN | 0
ENOC | ZOOM4002 | DXB | Busted lights chiller and selling area. | ATTENDED | SARAVANAN | 2
ENOC | ZOOM4002 | DXB | Busted lights chiller and selling area. | COMPLETED | SARAVANAN | 2
ENOC | ZOOM4002 | DXB | WATER LEAK FROM CHILLER#3 | COMPLETED | SARAVANAN | 3
ENOC | ZOOM4002 | DXB | WATER LEAK FROM CHILLER#3 | COMPLETED | SABITH ALI | 3
ENOC | ZOOM4009 | DXB | All chiller are leaking | ATTENDED | SABITH ALI | 3
ENOC | ZOOM4009 | DXB | chiller 3 water leaking | ATTENDED | SARAVANAN | 2
ENOC | ZOOM4009 | DXB | chiller 3 water leaking | COMPLETED | SARAVANAN | 2
ENOC | ZOOM4009 | DXB | CHILLER WATER LEAK | ATTENDED | SABITH ALI | 3
ENOC | ZOOM4009 | DXB | CHILLER WATER LEAK | COMPLETED | SABITH ALI | 3
ENOC | ZOOM4009 | DXB | water leak at chiller number 2. | ATTENDED | SARAVANAN | 1
ENOC | ZOOM4016 | DXB | OPEN CHILLER NOISE AND HIGH TEMP | COMPLETED | SARAVANAN | 0
ENOC | ZOOM4016 | DXB | OPEN CHILLER WATER LEAK | ATTENDED | SARAVANAN | 2
ENOC | ZOOM4016 | DXB | OPEN CHILLER WATER LEAK | COMPLETED | SARAVANAN | 2
ENOC | ZOOM4052 | DXB | Chiller 02 for chilled item not working | COMPLETED | SARAVANAN | 1
ENOC | 1025 | DXB | WALK IN CHILLER DOOR NOT CLOSING | ATTENDED | SADAM | 1
ENOC | 1077 | DXB | WALK IN FREEZER ICE FORMATION | COMPLETED | SARVANAN | 1
ENOC | 1077 | DXB | WALK IN FREEZER WATER LEAK | COMPLETED | SADAM | 1
ENOC | 1501 | DXB | DISPLAY CHILLER UNITS WATER LEAKAGE ISSUE | ATTENDED | SABITH ALI | 0
ENOC | 1058 | DXB | PPM | COMPLETED | MUTHUKUMAR | 1
ENOC | 4037 | DXB | OPEN CHILLER WATER LEAKAG | COMPLETED | SARAVANAN | 1
ENOC | 4037 | (blank) | CHILLER TEMP.GAUGE | COMPLETED | SARAVANAN | 1
ENOC | 4037 | (blank) | EQUITY WATER LEAK | COMPLETED | SABITH ALI | 0
ENOC | 1064 | DXB | VERTICAL CHILLER RUBBER GASKET | ATTENDED | MUSTAFA | 0
ENOC | 1236 | AJM | door freezer light not working | ATTENDED | VIGNESH | 1
ENOC | 1505 | DXB | OPEN CHILLER HIGH TEMP | COMPLETED | RACEL | 0
ENOC | 1047 | DXB | WALK-IN FREEZER | NOT ATTENDED | (blank) | 1
ENOC | 1047 | DXB | WLK IN FREEZER DRAIN LINE LEAKAG | COMPLETED | MOHAMMED | 0
ENOC | 1083 | DXB | PPM | COMPLETED | MUTHUKUMAR | 0
ENOC | 1507 | DXB | Walking Chiller temperature abnormal | COMPLETED | VIGNESH | 2
ENOC | 1507 | FUJ | WALKIN CHILLER TEMP ABNORMAL | COMPLETED | VIGNESH | 2
ENOC | 1203 | SHJ | PRONTO SECTION TABLE CHILLER NOT WORKING | COMPLETED | SABITH ALI | 1
ENOC | 1666 | DXB | PPM | COMPLETED | MUTHUKUMAR | 0
ENOC | 1143 | SHJ | OPEN CHILLER CBINET WATER LEAKAGE | COMPLETED | SABITH ALI | 1
ENOC | 1143 | SHJ | Open Chiller Drainage blocked | COMPLETED | RACEL | 1
ENOC | 1082 | DXB | PRONTO CHILLER LIGHT NOT WORKING | COMPLETED | SARVANAN | 1
ENOC | 1030 | DXB | WALK IN CHILLER HIGH TEMP | COMPLETED | SADAM | 0
ENOC | 4014 | DXB | WATER LEAKAGE | NOT ATTENDED | (blank) | 3
ENOC | 4014 | DXB | water leaking in the chiller | COMPLETED | SARVANAN | 3
ENOC | 4014 | DXB | water leaking in the chiller | NOT ATTENDED | (blank) | 3
ENOC | 1044 | DXB | Walking freezer door not closing proper | COMPLETED | SHABEEB | 1
ENOC | 1044 | DXB | Ice forming at walking freezer. | COMPLETED | SHABEEB | 1
ENOC | 1069 | DXB | PPM | COMPLETED | BIJU | 0
ENOC | 1069 | DXB | Walk-in Chiller high temperature | COMPLETED | BIJU | 1
ENOC | 1069 | DXB | FREEZER SHUT DOUN | COMPLETED | SARAVANAN | 0
ENOC | 1008 | (blank) | display chiller, temperature is high | COMPLETED | SADAM | 1
ENOC | 1043 | (blank) | WALK IN FREEZER ICE FORMATION | ATTENDED | SARAVANAN | 1
ENOC | 6568 | (blank) | Door Freezer | COMPLETED | (blank) | 1
ENOC | 1632 | DXB | PPM | COMPLETED | BIJU | 0
ENOC | 1602 | DXB | VERTICAL FREEZER TEMP ISSUE | NOT ATTENDED | (blank) | 0
EVERMORE | DIP | DXB | PPM | COMPLETED | MUTHUKUMAR | 1
EVERMORE | DIP | DXB | UNIT 1 & 2 TEMP ISSUE | COMPLETED | SHAFI | 1
EVERMORE | DIP | DXB | WATER LEAK FROM THE INSULATION | ATTENDED | MOHAMMED | 2
EVERMORE | DIP | DXB | WATER LEAK FROM THE INSULATION | COMPLETED | MOHAMMED | 2
EVERMORE | DIP | DXB | WATER LEAKAGE | COMPLETED | MOHAMMED | 1
GMG | SAHARA MALL | SHJ | CABINETS SHIFTING | COMPLETED | ROGER, GOVIND | 2
GMG | SAHARA MALL | SHJ | FREEZER AND CHILLER CABINET DISMANTLING | COMPLETED | DENNIS, MUTHUKUMAR | 2
GOURMET | 1004 | AUH | FAN SOUND CONDENSOR | (blank) | (blank) | 1
GOURMET | 1004 | AUH | FREEZER AND CHILLER TEMP. ISSUE | ATTENDED | OLIVER | 1
GOURMET | 1004 | AUH | FREEZER NOISE ISSUE | ATTENDED | (blank) | 2
GOURMET | 1004 | AUH | FREEZER NOISE ISSUE | COMPLETED | RANDOLPH | 2
GOURMET | 1004 | AUH | FREEZER NOT WORKING | ATTENDED | RANDOLPH | 1
GOURMET | 1004 | AUH | PORKSECTION FREEZER TEMP ISSUE | ATTENDED | OLIVER | 2
GOURMET | 1004 | AUH | PORKSECTION FREEZER TEMP ISSUE | COMPLETED | OLIVER | 2
GOURMET | 1004 | AUH | PPM | (blank) | (blank) | 1
GOURMET | AL GHURAIR | DXB | COLD ROOM TEMP. ISSUE | NOT ATTENDED | SADAM | 1
GOURMET | AL REEM | AUH | CHILLER HIGH TEMP | ATTENDED | OLIVER | 2
GOURMET | AL REEM | AUH | CHILLER HIGH TEMP | COMPLETED | OLIVER | 2
GOURMET | 1004 AL REEM | AUH | PPM / MARKET AREA | COMPLETED | FROILAN | 2
GOURMET | 1004 AL REEM | AUH | PPM / KITCHEN AREA | COMPLETED | FROILAN | 2
GOURMET | 1004 AL REEM | AUH | ICE CREAM FREEZER NOT WORKING | COMPLETED | OLIVER | 1
GOURMET | 1004 AL REEM | DXB | CONDENSOR FAN MOTOR NOT WORKING | COMPLETED | FROILAN | 0
GRANDIOSE | AL BUSTAN | AUH | CHILLER HIGH TEMP | ATTENDED | FROILAN | 1
GRANDIOSE | AL SAHEL | AUH | CHILLER UNIT NOT WORKING | COMPLETED | OILVER | 1
GRANDIOSE | AL SAHEL | AUH | JUICE CHILLER HIGH TEMP | COMPLETED | RANDOLPH | 2
GRANDIOSE | AL SAHEL | AUH | JUICE CHILLER HIGH TEMP | COMPLETED | RANDOLPH, TROVEE | 2
GRANDIOSE | AL SOYOUH | SHJ | COLD ROOM FREEZER NOT COOLING | ATTENDED | DENNIS, ROGER | 3
GRANDIOSE | AL SOYOUH | SHJ | COLD ROOM FREEZER NOT WORKING | ATTENDED | RACEL | 2
GRANDIOSE | AL SOYOUH | SHJ | COLD ROOM FREEZER NOT WORKING | COMPLETED | VIGNESH, SELVAN, SUDHEESH | 2
GRANDIOSE | AL SOYOUH | SHJ | COLOD ROOM MONOBLOCK UNIT NOT COOLING | COMPLETED | AHSAN | 3
GRANDIOSE | AL SOYOUH | SHJ | COMPRESSOR REPLACEMNET FOR MONO BLOCK | COMPLETED | DENNIS | 2
GRANDIOSE | AL SOYOUH | SHJ | INSTALLTION OF EVP FAN MOTOR AND PCB BOARD | COMPLETED | DENNIS, ROGER | 3
GRANDIOSE | AL SOYOUH | SHJ | WALKIN FREEZER HIGH TEMP | ATTENDED | RACEL | 2
GRANDIOSE | B1 MALL | DXB | FREEZER NOT WORKING | COMPLETED | SHAFI | 4
GRANDIOSE | BIN SHABIB MALL | DXB | FREEZER ISSUE DOOR , MILK YOUGUT CHILLER SLIDING | ATTENDED | SADAM | 1
GRANDIOSE | HOOR 17 | DXB | CDU ISTALLATION FOR RECEIVING AREA | COMPLETED | DENNIS, SHAFI, SABITH | 2
GRANDIOSE | HOOR 17 | DXB | CDU ISTALLATION FOR RECEIVING AREA | COMPLETED | SHAFI, SABITH, SARAVANAN | 2
GRANDIOSE | HOOR 17 | DXB | FREEZER TEMP ISSUE. | COMPLETED | SHABEEB | 1
GRANDIOSE | JUNTION MALL DIP | DXB | CHILLERS NOT WORKING | ATTENDED | SHABIB | 1
GRANDIOSE | MASDAR CITY | AUH | CHEESE CHILLER TEMP.ISSUE | ATTENDED | RANDOLPH | 1
GRANDIOSE | WASL VILLAGE | DXB | PORK SECTION TEMP ISSUE | ATTENDED | RACEL | 2
GRANDIOSE | WASL VILLAGE | DXB | PORK SECTION TEMP ISSUE | COMPLETED | VIGNESH | 2
GRANDIOSE | SOUQ AL BAHAR | DXB | NEED TO CHECK COMPRESSOR | ATTENDED | SADAM | 4
GRANDIOSE | SOUQ AL BAHAR | DXB | NEED TO CHECK COMPRESSOR | ATTENDED | (blank) | 4
GRANDIOSE | SOUQ AL BAHAR | DXB | NEED TO CHECK COMPRESSOR | COMPLETED | SADAM | 4
GRANDIOSE | SOUQ AL BAHAR | DXB | NEED TO CHECK COMPRESSOR | COMPLETED | SARAVANAN | 4
GRANDIOSE | AL WASL | DXB | MEET FREEZER TEMP.ISSUE | COMPLETED | MOHAMMED | 1
HOP | JEBAL ALI | DXB | COLD ROOM DOOR ICE FORMATION | ATTENDED | SADAM | 1
HOP | JEBAL ALI | DXB | COLD ROOM DOOR NOT CLOSING | ATTENDED | SARAVANAN | 2
HOP | JEBAL ALI | DXB | COLD ROOM ICE FORMATION | ATTENDED | SARAVANAN | 4
HOP | JEBAL ALI | DXB | COLD ROOM TEMP. ISSUE | ATTENDED | (blank) | 1
HOP | JEBAL ALI | DXB | ELCB TRIPPING AND DRAIN TRAY FULL ICE | COMPLETED | MUTHUKUMAR | 1
HOP | JEBAL ALI | DXB | FREEZER COLD ROOM DOOR CHECK | COMPLETED | SARAVANAN | 2
HOP | JEBAL ALI | DXB | PACKING ROOM AC NOT WORKING ALSO NEW DOOR HANDLE NOT WORKING | ATTENDED | MOHAMMED | 4
HOP | JEBAL ALI | DXB | PPM | COMPLETED | MUTHUKUMAR | 1
HOP | JEBAL ALI | DXB | PPM | COMPLETED | SUDHEESH | 37
HOP | JABAL ALI | DXB | FEMALE CHANGING ROOM AC NOT WORKING | NOT ATTENDED | (blank) | 1
LULU | AL AIN CENTER | AL AIN | JUICE CHILLER NOISE ISSUE | COMPLETED | TALIB | 1
LULU | AL KAHIR | AL AIN | EVALUATION OF USE AND OLD LUGIN FREEZER CABINET | COMPLETED | TALIB | 1
LULU | AL KHARIR | AL AIN | FISH CHILLER COLD ROOM DOOR HANDLE ISSUE | COMPLETED | TALIB | 1
LULU | AL KHARIR | AL AIN | MILK CHILLER HIGH TEMP | ATTENDED | TALIB | 1
LULU | AL QUAA | AUH | WATER LEAK IN FRUIT CHILLER | COMPLETED | TALIB | 1
LULU | AL RAFFA | DXB | CHILLER HIGH TEMP.ISSUE | COMPLETED | MUTHUKUMAR | 1
LULU | AL RAFFA | DXB | COLD ROOM LIGHT NOT WORKING | COMPLETED | SADAM | 1
LULU | AL WATHBA | AUH | WATER LEAK AND LIGHT NOT WORKING | ATTENDED | OLIVER | 4
LULU | DHAID | SHJ | BACK STORE FREEZER 1 COMPRESSOR NOT WORKING | COMPLETED | VIGNESH | 1
LULU | DHAID | SHJ | MILK CHILLER TRIPPING | COMPLETED | AHSAN | 1
LULU | DIP | DXB | FREEZER 21 ITEMS IN TOP MELTING(TEMP NORMAL) | NOT ATTENDED | (blank) | 1
LULU | DIP | DXB | FREEZER CABINET GAS LEAK | COMPLETED | MOHAMMED | 2
LULU | DIP | DXB | FREEZER COLD ROOM DEF SETTING NEED TO CHANGE / FREEZER NOISE ISSUE | COMPLETED | SHAFI | 1
LULU | DIP | DXB | FREEZER COLD ROOM HIGH TEMP | ATTENDED | MOHAMMED | 2
LULU | DIP | DXB | FREEZER NOISE ISSUE | COMPLETED | MOHAMMED | 1
LULU | DIP | DXB | ICE MACHINE NOT WORKING | ATTENDED | SHAFI | 1
LULU | DIP | DXB | LIGHT NOT WORKING | ATTENDED | SADAM | 1
LULU | DIP | DXB | COMPRESSOR ICE FORMATION | COMPLETED | MOHAMMED | 1
LULU | DIP | DXB | FREEZER IS NOT WORKING | COMPLETED | SHAFI/DENNIS | 1
LULU | JADHAF | DXB | BAKERY CHILLER COMMISSIONG | COMPLETED | SARAVANAN | 1
LULU | MAQAM | AL AIN | BACK STORE COLD ROOM TEMP ISSUE | COMPLETED | TALIB | 1
LULU | MAQAM | AL AIN | CHEESE CHILLER LIGHT NOT WORKING | ATTENDED | TALIB | 3
LULU | MAQAM | AL AIN | CHEESE CHILLER LIGHT NOT WORKING | COMPLETED | TALIB | 6
LULU | MAQAM | AL AIN | FISH COLD ROOM CHILLER LIGHT NOT WORKING | ATTENDED | TALIB | 1
LULU | MAQAM | AL AIN | FREEZER COLD ROOM HIGH TEMP | COMPLETED | TALIB | 1
LULU | NUAIMIA | AJM | CHEESE DELI CHILLER TEMP ISSUE. | COMPLETED | VIGNESH | 1
LULU | NUAIMIA | AJM | CHILLER TEMP AND ICE FORMATION ISSUE | ATTENDED | RACEL | 2
LULU | NUAIMIA | AJM | CHILLER#1 & #2 TEMP AND ICE FORMATION ISSUE | COMPLETED | RACEL | 2
LULU | NUAIMIA | AJM | EGG CHILLER GETTING NEGATIVE TEMP | COMPLETED | AHSAN | 1
LULU | NUAIMIA | AJM | HOT FOOD CHILLER GETTING TOO MUCH COLD | ATTENDED | RACEL | 1
LULU | NUAIMIA | AJM | VEG CHILLER TEMP ISSUE. | ATTENDED | AHSAN | 2
LULU | NUAIMIA | AJM | VEG CHILLER TEMP ISSUE. | ATTENDED | (blank) | 2
LULU | NUAIMIA | AJM | VEG COLD ROOM CHILLER WTAER LEAK | COMPLETED | RACEL | 1
LULU | NUAIMIA | DXB | HOT FOOD CHILLER UNIT TOO MUCH COLD | ATTENDED | RACEL | 1
LULU | NUAIMIA | SHJ | BUTCHERY CHILLER HIGH TEMP. | COMPLETED | RACEL | 1
LULU | OLIVE TOWER | AUH | COLD ROOM FREEZER BUSTED LIGHT | COMPLETED | OLIVER | 2
LULU | OLIVE TOWER | AUH | EATER LEAKAGE IN LABAN UP CHILLER | COMPLETED | TROVEE | 1
LULU | OLIVE TOWER | AUH | FREEZER ROOM TUBE LIGHTR NOT WORKING | ATTENDED | OLIVER | 2
LULU | OLIVE TOWER | AUH | VEGETABLE CHILLER NOT WORKING | ATTENDED | TROVEE | 1
LULU | TCA | AUH | FROZEN VEG.PLUG IN UNIT TEMP. ISSUE | ATTENDED | RANDOLPH | 1
LULU | AL AIN | AL AIN | DISPLAY CHILLER ARE NOT WORKING | COMPLETED | TALIB | 1
LULU | AL WATHBA | AUH | SMELL ISSUE AND WATER LEAKAGE | COMPLETED | FROILAN | 1
LULU | AL WATHBA | AUH | MILK CHILLER SMELL BAD | COMPLETED | FROILAN | 1
LULU | DHAID | SHJ | FREEZER COLD ROOM TEMP ISSUE. | ATTENDED | AHSAN | 1
LULU | DHAID | SHJ | COLD ROOM FREEZER HIGH TEMP. | ATTENDED | RACEL | 1
LULU | DIP | DXB | FREEZER TRIP ISSUE | ATTENDED | MOHAMMED | 1
LULU | MAQAM | AL AIN | CHEESE DISPLAY CHILLER LIGHT NOT WOTKING | ATTENDED | TALIB | 2
LULU | MAQAM | AL AIN | CHEESE DISPLAY CHILLER LIGHT NOT WOTKING | COMPLETED | TALIB | 2
LULU | MAQAM | AL AIN | COLD ROOM LOCK ISSUE | ATTENDED | TALIB | 1
LULU | MAQAM | AL AIN | CHILLER COLD ROOM BURNING SMELL ISSUE. | ATTENDED | TALIB | 1
LULU | NUAIMIA | AJM | BAKERY CHILLER NOT WORKING | COMPLETED | VIGNESH | 1
LULU | NUAIMIA | SHJ | HOT FOOD CHILLER TEMP ISSUE | (blank) | (blank) | 1
LULU | OLIVE TOWER | AUH | WATER LEAKAGE | COMPLETED | RANDOLPH | 1
LULU | SAADIYAT | AUH | FISH COLD ROOM HIGH TEMP ISSUE | COMPLETED | RANDOLPH | 4
LULU | OUD METHA | DXB | BUTCHERY DISPLAY HIGH TEMP & VEG CHILLER WATER LEAK | COMPLETED | SARVANAN | 1
LULU | AL KHAIR | AL AIN | FREEZER WATER LEAKAGE | COMPLETED | TALIB | 1
LULU | TERRACE MALL | KWT | PLUG IN FREEZER AN AND COLD ROOM BAKERY HIGH TEMP | COMPLETED | JOSE LITO | 1
LULU | AL FORSAN | AUH | FREEZER FAULTY ALARM | (blank) | (blank) | 1
NADEC | SHARJAH | SHJ | CHILLER COLD ROOM #2 EVP#1 & EVP#2 NOT COOLING | ATTENDED | SABITH ALI | 3
NADEC | SHARJAH | SHJ | COLD ROOM#1 TEMP ISSUE | ATTENDED | SABITH ALI | 3
NADEC | SHARJAH | SHJ | LOADING AREA CHILLE#2 NOT WORKING | ATTENDED | SABITH ALI | 3
NADEC | SHARJAH | SHJ | LOADING AREA#1 CHILLER NOT WORKING | ATTENDED | SABITH ALI | 1
NESTO | AL FAHIDI | DXB | CHILLER SHUTDOWN | COMPLETED | MOHAMMED | 1
NESTO | AJC | AJM | ALL FREEZERS HIGH TEMP | COMPLETED | GOVIND | 1
NESTO | AJC | AJM | COLD ROOM LIGHT NOT WORKING | COMPLETED | SABITH ALI | 2
NESTO | AJC | AJM | FISH SECTION BED FREEZER TEMP.ISSUE | COMPLETED | SABITH ALI | 2
NESTO | AJC | AJM | FREEZER COLD ROOM LIGHT NOT WORKING | COMPLETED | AHSAN | 1
NESTO | AJC | AJM | FREEZER HIGH TEMP | COMPLETED | AHSAN | 3
NESTO | AJC | AJM | ISLAND FREEZER HIGH TEMP | COMPLETED | ROGER | 1
NESTO | AJC | AJM | ISLAND FREEZER LEAK RECTIFICATION | ATTENDED | RACEL | 3
NESTO | AJC | AJM | ISLAND FREEZER NOT WORKING | COMPLETED | RACEL | 4
NESTO | AJC | AJM | ISLAND FREEZER SHUTDOWN | COMPLETED | AHSAN | 1
NESTO | AJC | AJM | PPM | COMPLETED | ABHIJITH | 2
NESTO | AJC | AJM | CHILLER COLD ROOM NOT WORKING AND ICE MACHINE | COMPLETED | SABITH ALI | 1
NESTO | AJC | AJM | ICE MACHINE NOT WORKING | ATTENDED | AHSAN | 1
NESTO | AJC | AUH | ICE MACHINE ISSUE | COMPLETED | AHSAN | 1
NESTO | AJC | DXB | WATER LEAKAGE | COMPLETED | VIGNESH | 2
NESTO | AJC | DXB | WATER LEAKAGE | NOT ATTENDED | (blank) | 2
NESTO | AJE | AJM | CHILLER ICE FORMATION | COMPLETED | VIGNESH | 1
NESTO | AJE | AJM | CHILLER TEMP NORMAL BUT NO COOLING | COMPLETED | RACEL | 1
NESTO | AJE | AJM | CHILLER TEMP.ISSUE | COMPLETED | AHSAN | 1
NESTO | AJE | AJM | DELI CHILELR EVP COIL INSTALLATION | COMPLETED | BIJU | 2
NESTO | AJE | AJM | DELI CHILLER TEMP ISSUE. | ATTENDED | VIGNESH | 2
NESTO | AJE | AJM | DELI CHILLER TEMP ISSUE. | COMPLETED | VIGNESH | 2
NESTO | AJE | AJM | DELICATE COUNTER UNIT#1 EVP FIXING | COMPLETED | AHSAN | 2
NESTO | AJE | AJM | F&V CHILLER AND DAIRY SECTION NOT COOLING PROPERLY | COMPLETED | RACEL | 1
NESTO | AJE | AJM | FREEZERN NOT WORKING | COMPLETED | RACEL | 1
NESTO | AJE | AJM | ICE MACHINE NOT WORKING | ATTENDED | SABITH ALI | 2
NESTO | AJE | AJM | INSPECTION OF HOT FOOD SWEAT COUNTER, BAKERTY COUNTER AND DISPLAY CHILLERS | COMPLETED | SABITH ALI | 1
NESTO | AJE | AJM | ISLAND FREEZER HIGH TEMP | COMPLETED | VIGNESH | 1
NESTO | AJE | AJM | ISLAND FREEZER TEMP ISSUE | COMPLETED | SELVAN | 1
NESTO | AJE | AJM | MONTHLY REPORT | COMPLETED | RACEL | 4
NESTO | AJE | AJM | PPM | COMPLETED | ABHIJITH | 1
NESTO | AJE | AJM | VEG CHILLER HIGH TEMP | COMPLETED | RACEL | 1
NESTO | AJE | AJM | (blank) | NOT ATTENDED | RACEL | 1
NESTO | AJE | AJM | HOT CABIN ISSUE. | ATTENDED | AHSAN | 3
NESTO | AJE | AJM | HOT CABIN ISSUE. | COMPLETED | AHSAN | 3
NESTO | AJE | AJM | CHILLERS TEMP ISSUE. | COMPLETED | RACEL | 1
NESTO | AJE | AJM | BACK STORE CHILLER TEMP. ISSUE | ATTENDED | RACEL | 1
NESTO | AJE | AJM | NEED TO INSPECT ALL UNIT HOT FOOD | COMPLETED | AHSAN | 3
NESTO | AJE | AJM | FISH SECTIONCHILLER NOT WORKING | ATTENDED | SABITH ALI | 2
NESTO | AJE | AJM | ICE MACHINE DAMAGE | ATTENDED | AHSAN | 2
NESTO | AJE | AJM | ICE MACHINE DAMAGE | ATTENDED | RACEL | 2
NESTO | AJE | AJM | FREEZER ROOM LIGHT NOT WORKING | COMPLETED | RACEL | 1
NESTO | AJE | AJM | DELI SECTION TEMP ISSUE | COMPLETED | RACEL | 2
NESTO | AJE | AJM | DELI SECTION TEMP ISSUE | NOT ATTENDED | (blank) | 2
NESTO | AJE | AJM | BUTCHERY COLD ROOM MONOBLOCK WATER LEAKING | ATTENDED | AHSAN | 2
NESTO | AJE | AJM | BUTCHERY COLD ROOM MONOBLOCK WATER LEAKING | COMPLETED | AHSAN | 2
NESTO | AJE | AJM | F & V CHILLER TEMP ISSUE | (blank) | (blank) | 1
NESTO | AJE | DXB | PPM | COMPLETED | ABHIJITH | 1
NESTO | AJE | DXB | CAKE DISPLAY TEMP. ISSUE | COMPLETED | RACEL | 1
NESTO | AJE | SHJ | EGG CHILLER NOT WORKING | COMPLETED | VIGNESH | 1
NESTO | AJF | AJM | BACK STORE CHILLER EVP ICE FORMATION | ATTENDED | VIGNESH | 1
NESTO | AJF | AJM | BUTCHERY STEEL BODY CHILLER DOOR ISSUE | ATTENDED | RACEL | 4
NESTO | AJF | AJM | DELI CHILLER HIGH TEMP ISSUE | ATTENDED | AHSAN | 2
NESTO | AJF | AJM | DELI CHILLER HIGH TEMP ISSUE | COMPLETED | SABITH ALI | 2
NESTO | AJF | AJM | DELI CHILLER TEMP ISSUE. | ATTENDED | AHSAN | 1
NESTO | AJF | AJM | DOOR SWITCH CHECK IN COLD ROOM | COMPLETED | AHSAN | 1
NESTO | AJF | AJM | MONTHLY REPORT | COMPLETED | RACEL | 4
NESTO | AJF | AJM | RE-INSULATION OF FREEZER#1 | ATTENDED | RACEL | 3
NESTO | AJF | AJM | WATER LEAK IN THE FREEZER | ATTENDED | VIGNESH | 6
NESTO | AJG | AJM | CHILLER LIGHT NOT WORKING | ATTENDED | AHSAN | 4
NESTO | AJG | AJM | COLD ROOM LIGHT NOT WORKING | (blank) | (blank) | 1
NESTO | AJG | AJM | DISPLAY FREEZER ICE FORMATION | NOT ATTENDED | RACEL | 1
NESTO | AJG | AJM | FREEZER COLD ROOM NOT WORKING | COMPLETED | VIGNESH | 1
NESTO | AJG | AJM | FREEZER LIGHT NOT WORKING | ATTENDED | AHSAN | 1
NESTO | AJG | AJM | FREEZER TEMP NORMAL BUT NO COOLING | COMPLETED | SABITH ALI | 4
NESTO | AJG | AJM | FREEZER, DELICATE, BUTCHERY OPEN CHILLER LIGHT REPLACEMENT / FREEZER LIGHTS AND DELICATE LIGHTS | COMPLETED | AHSAN | 1
NESTO | AJG | AJM | MONTHLY REPORT | COMPLETED | RACEL | 4
NESTO | AJG | AJM | VEGETABLE BACK STORE DOOR NOT CLOSING | ATTENDED | AHSAN | 1
NESTO | AJG | AJM | DELI CHILLER BACK STORE LIGHT NOT WORKING | COMPLETED | VIGNESH | 1
NESTO | AJG | AJM | FREEZER NO .6 TEMP ISSUE | COMPLETED | RACEL | 1
NESTO | AJG | AJM | CHILLER BACK STORE AND DISPLAY CHILLER LIGHT NOT WORKING | COMPLETED | RACEL | 1
NESTO | AJJ | AJM | BUTCHERY CHILLER HIGH TEMP | COMPLETED | RACEL | 2
NESTO | AJJ | AJM | BUTCHERY CHILLER HIGH TEMP | COMPLETED | VIGNESH | 2
NESTO | AJJ | AJM | CHILLER SENSOR COMPLAINT FISHERY | ATTENDED | RACEL | 1
NESTO | AJJ | AJM | FREEZER TEMP.ISSUE | COMPLETED | RACEL | 1
NESTO | AJJ | AJM | ICE CREAM FREEZER TEMP ISSUE | COMPLETED | TALIB | 1
NESTO | AJJ | AJM | FREEZER TEMP. NORMAL BUT LOW AIR FLOW | COMPLETED | AHSAN | 1
NESTO | AL AIN | AL AIN | CABINET INDOOR SERVICE | COMPLETED | TALIB | 37
NESTO | AL AIN | AL AIN | CHILLER TEMP ISSUE. | COMPLETED | TALIB | 1
NESTO | AL AIN | AL AIN | COLD ROOM TEMP. ISSUE | COMPLETED | TALIB | 1
NESTO | AL AIN | AL AIN | END WALL BROKEN | ATTENDED | TALIB | 1
NESTO | AL AIN | AL AIN | FREEZER COLD ROOM TEMP.ISSUE | COMPLETED | TALIB | 1
NESTO | AL AIN | AL AIN | FREEZER LOW COOLING | COMPLETED | TALIB | 1
NESTO | AL AIN | AL AIN | FREEZER TEMP ISSUE. | (blank) | (blank) | 1
NESTO | AL AIN CENTER | AL AIN | BAKERY SECTION CHILLER NOT WORKING | ATTENDED | VIGNESH | 1
NESTO | AL AIN CENTER | AL AIN | BUTCHERY CHILLER FAN NOT WORKING | COMPLETED | TALIB | 1
NESTO | AL AIN CENTER | AL AIN | FREEZER#9 ITEMS MELTING | COMPLETED | TALIB | 2
NESTO | AL AIN CENTER | AL AIN | HOT FOOD FOOD CHILLER HIGH TEMP / BUTCHERY CHILLER TEMP VARIATION AND FREEZER ITEMS MELTING | COMPLETED | TALIB | 2
NESTO | AL FAHIDI | DXB | BAKERY CHILLER ICE FORMATION | (blank) | (blank) | 1
NESTO | AL FAHIDI | DXB | ICE FORMATION | ATTENDED | SHAFI | 2
NESTO | AL FAHIDI | DXB | ICE FORMATION | COMPLETED | MOHAMMED | 2
NESTO | AL FAHIDI | DXB | ISLAND FREEXZER SHUTDOWN | COMPLETED | SHAFI | 1
NESTO | AL FAHIDI | DXB | SOFT DRINKS CHILLER WATER LEAK | COMPLETED | SADAM | 1
NESTO | AL FAHIDI | DXB | BUTCHERY CHILLER TCE FORMATION | ATTENDED | SHABEEB | 1
NESTO | AL FAHIDI | DXB | VEG CHILLER WATER LEAK | ATTENDED | SABITH ALI | 1
NESTO | AL MINA | DXB | FREEZERS TEMP.ISSUE | COMPLETED | RACEL/MOHAMMED/SARAVANAN | 4
NESTO | AL MINA | DXB | HOT FOOD CHILLER TEMP ISSUE | COMPLETED | SADAM | 1
NESTO | AL MINA | DXB | WATER LEAKAGE | ATTENDED | SADAM | 6
NESTO | AL MINA | DXB | WATER LEAKAGE | NOT ATTENDED | (blank) | 3
NESTO | AL MINA | DXB | DELI SECTION WATER LEAKAG | COMPLETED | MOHAMMED | 1
NESTO | ARJAN | DXB | CHILLER CABINETS ARE NOT WORKING | COMPLETED | MOHAMMED | 1
NESTO | ARJAN | DXB | CHILLER NEED TO SERIVE AND CHECK THE PRESSURE | COMPLETED | SHAFI | 1
NESTO | ARJAN | DXB | ICE FORMATION | COMPLETED | SADAM | 1
NESTO | ARJAN | DXB | ICE MACHINE NOT WORKING | ATTENDED | SARAVANAN | 1
NESTO | ARJAN | DXB | OPEN CHILLER HIGH TEMP | COMPLETED | SADAM | 1
NESTO | FAKRUDDIN MALL | AJM | ICE MACHINE LESS PRODUCTION | COMPLETED | AHSAN | 1
NESTO | FUJAIRAH MALL | FUJ | ALL FREEZER NO COOLING | ATTENDED | RACEL | 1
NESTO | FUJAIRAH MALL | FUJ | BAKERY CHILLER HIGH TEMP | ATTENDED | SABITH ALI | 1
NESTO | FUJAIRAH MALL | FUJ | FREEZER CABINET HIGH TEMP | COMPLETED | SABITH ALI | 1
NESTO | FUJAIRAH MALL | FUJ | FREEZER HIGH TEMP | ATTENDED | RACEL | 2
NESTO | FUJAIRAH MALL | FUJ | FREEZER NOISE ISSUE | COMPLETED | RACEL | 1
NESTO | FUJAIRAH MALL | FUJ | FREEZER SOUND ISSUE | COMPLETED | RACEL | 1
NESTO | FUJAIRAH MALL | FUJ | HOT FOOD SECTION EVP GAS LEKAGE / BUTCHERY COLD ROOM SLIDING DOOR STUCK | ATTENDED | AHSAN | 1
NESTO | FUJAIRAH MALL | FUJ | ISLAND FREEZER MOISTURE ISSUE | COMPLETED | RACEL | 2
NESTO | FUJAIRAH MALL | FUJ | ISLAND FREEZER NOISE ISSUE | COMPLETED | VIGNESH | 1
NESTO | FUJAIRAH MALL | FUJ | WATER LEAK FROM THE INSULATION | COMPLETED | VIGNESH | 1
NESTO | FUJEIRAH | FUJ | CHILLER CABINETS TEMP ISSUE | COMPLETED | VIGNESH | 1
NESTO | FUJEIRAH | FUJ | FREEZER WATER LEAK | COMPLETED | VIGNESH | 1
NESTO | FUJEIRAH | FUJ | WATER LEAKAGE | COMPLETED | RACEL | 1
NESTO | FUJEIRAH | FUJ | SALAD SECTION TEMP ISSUE | COMPLETED | VIGNESH | 1
NESTO | FUJEIRAH | FUJ | DELI CHILLER TRMP ISSUE | COMPLETED | AHSAN | 1
NESTO | FUJEIRAH | FUJ | HEAVY NOISE ISSUE | (blank) | (blank) | 1
NESTO | KARAMA | AJM | COMBI FREEZER TRIPPING ISSUE / FREEZER COLD ROOM LIGHT NOT WORKING | COMPLETED | SHAFI | 1
NESTO | KARAMA | DXB | BAKERY CHILLER TRIPPING ISSUE | ATTENDED | SARAVANAN | 1
NESTO | KARAMA | DXB | BAKERY DISPLAY TEMP ISSUE. | ATTENDED | SADAM | 1
NESTO | KARAMA | DXB | BUTCHERY CHILLER AND FISHERY CHILLER DISPLAY CHECK | ATTENDED | SHAFI | 3
NESTO | KARAMA | DXB | BUTCHERY CHILLER AND FISHERY CHILLER DISPLAY CHECK | ATTENDED | (blank) | 3
NESTO | KARAMA | DXB | BUTCHERY CHILLER AND FISHERY CHILLER DISPLAY CHECK | COMPLETED | SHAFI | 3
NESTO | KARAMA | DXB | COLD ROOM LIGHT NOT WORKING | COMPLETED | SARVANAN | 1
NESTO | KARAMA | DXB | COMBI FREEZER LIGHT NOT WORKING | ATTENDED | MOHAMMED | 1
NESTO | KARAMA | DXB | DISPLAY FREEZER LIGHT NOT WORKING | COMPLETED | SHAFI | 1
NESTO | KARAMA | DXB | LIGHTS CHECK | COMPLETED | MUTHUKUMAR | 1
NESTO | KARAMA | DXB | PARKING AREA INSULATION REPLACEMENT | COMPLETED | ROGER | 1
NESTO | KARAMA | DXB | CHEESE UNIT TEMP ISSUE FREEZER NO 4 ,5 | COMPLETED | SADAM | 1
NESTO | KARAMA | DXB | BAKERY CHILLRE NOT WORKING | (blank) | (blank) | 1
NESTO | MALEHA | SHJ | BUTCHERY CHILLER HIGH TEMP. | COMPLETED | VIGNESH | 1
NESTO | MALEHA | SHJ | CHILLER WATER LEAK AND CHILLER HIGH TEMP | COMPLETED | SABITH ALI | 1
NESTO | MALEHA | SHJ | FROZON CABINET | ATTENDED | (blank) | 1
NESTO | MALEHA | SHJ | SALAD COUNTER TEMP ISSUE. | ATTENDED | SABITH ALI | 2
NESTO | MALEHA | SHJ | SALAD COUNTER TEMP ISSUE. | NOT ATTENDED | (blank) | 2
NESTO | MAYSALOON | SHJ | BUTCHERY CHILLER TEAMP OKAY BUT ITEMS FROSTING | COMPLETED | SABITH ALI | 2
NESTO | MAYSALOON | SHJ | BUTCHERY CHILLER TEAMP OKAY BUT ITEMS FROSTING | NOT ATTENDED | SABITH ALI | 2
NESTO | MAYSALOON | SHJ | FISH COLD ROOM LIGHT NOT WORKING | ATTENDED | VIGNESH | 1
NESTO | MAYSALOON | SHJ | PPM ALL CHILLER CABINETS AND FREEZER CABINETS | COMPLETED | VIGNESH | 1
NESTO | MUWAILHA | SHJ | CHEESE CHILLER HIGH TEMP | COMPLETED | VIGNESH | 1
NESTO | MUWAILHA | SHJ | DAIRY CHILELR WATER LEAK | ATTENDED | AHSAN | 1
NESTO | MUWAILHA | SHJ | FREEZER COLD ROOM TEMP ISSUE AND LIGHT NOT WORKING | COMPLETED | BIJU | 1
NESTO | MUWAILHA | SHJ | FREEZER HEADER CABINET NOISE ISSUE | COMPLETED | VIGNESH | 1
NESTO | MUWAILHA | SHJ | ICE MACHINE NOT WORKING | COMPLETED | AHSAN | 1
NESTO | SATWA | DXB | DELI CHILLER WTAER LEAK / ALL COLD ROOM DOOR HANDLE CHECK | ATTENDED | SADAM | 1
NESTO | SATWA | DXB | FREEZER NOT COOLING | COMPLETED | RACEL | 1
NESTO | SATWA | DXB | FREEZER NOT WORKING | ATTENDED | SABITH ALI | 2
NESTO | SATWA | DXB | ISLAND FREEZER NOISE ISSUE | COMPLETED | SHAFI | 1
NESTO | SATWA | DXB | EGG PAROTTA CHILLER | COMPLETED | SADAM | 1
NESTO | SATWA | DXB | BUTCHERY SECTION TEMP ISSUE | COMPLETED | AHSAN | 2
NESTO | SATWA | DXB | SALAD SECTION TEMP ISSUE | COMPLETED | AHSAN | 1
NESTO | SATWA | DXB | BUTCHERY SECTION CHILLER TEMP .ISSUE | ATTENDED | RACEL | 2
NESTO | WAREHOUSE | DXB | COMPRESSOR AREA ICE FORMATIONA AND WATER LEAK | ATTENDED | SADAM | 4
NESTO | WAREHOUSE | DXB | COMPRESSOR SHUTDOWN | ATTENDED | MOHAMMED | 1
NESTO | WAREHOUSE | DXB | ICE MACHINE ISSUE / COMPRESSOR HAVE ICE FORMATION | COMPLETED | AHSAN | 2
NESTO | WAREHOUSE | DXB | OUTSIDE COOLING BLOWER NOISE ISSUE | ATTENDED | SABITH ALI | 1
NESTO | WAREHOUSE | DXB | RACK SYSTEM CONDENSER BLOWER BELT REPLACEMENT | COMPLETED | MOHAMMED | 2
NESTO | WAREHOUSE | DXB | WATER LEAKAGE | COMPLETED | SADAM | 2
NESTO | WAREHOUSE | DXB | WATER LEAKAGE | NOT ATTENDED | (blank) | 2
NESTO | WAREHOUSE | DXB | DOOR LOCK NOT WORKING | ATTENDED | SADAM | 1
NESTO | WAREHOUSE | DXB | F & V CHILLER NOT WORKING | ATTENDED | SADAM | 1
NESTO | WAREHOUSE | DXB | COLD ROOM DOOR ISSUE | ATTENDED | SHABEEB | 2
NESTO | WAREHOUSE | DXB | COLD ROOM DOOR ISSUE | COMPLETED | SHABEEB | 2
NESTO | MUSAFFAH | AUH | ICE MACHINE NOT WORKING | COMPLETED | RANDOLPH | 1
NESTO | NADD AL HAMMAR | DXB | FZ 01 NOT WORKING | COMPLETED | MOHAMMED | 1
NESTO | AJF | AJM | DELI CHILLER HIGH TEMP. | COMPLETED | AHSAN | 1
NESTO | AJF | AJM | EGG CHILLER WATER LEAKAGE | COMPLETED | AHSAN | 1
NESTO | AJL | AJM | FREEZER NOT WORKING | COMPLETED | AHSAN | 1
NESTO | AJJ | AJM | CHILLER NO 1 NOT WORKING | COMPLETED | AHSAN | 1
NESTO | AJJ | AJM | BUTCHERY COUNTER NO 1 EVAPORATOR ICE AND CONTROLLER SHOWING ERROR | COMPLETED | AHSAN | 1
NESTO | AL AIN | AL AIN | RECHARGE GAS 10 NOS | COMPLETED | TALIB | 1
NESTO | AL AIN CENTER | AL AIN | BAKERY CHILLER NOT WORKING | COMPLETED | TALIB | 1
NESTO | KARAMA | DXB | WATER LEAK FROM VEGETABLE CHILLER PIPE LINE IN PARKING AREA | ATTENDED | MOHAMMED | 1
NESTO | MUWAILHA | SHJ | FREEZER COLD ROOM TEMP.ISSUE | COMPLETED | SABITH ALI | 1
NESTO | SATWA | DXB | FREEZER NOT WORKING | COMPLETED | SADAM | 2
PASONS | 28 | FUJ | CHILLER HIGH TEMP AND ALARM | COMPLETED | AHSAN | 1
PASONS | 28 | FUJ | CHILLER HIGH TEMP, SAME ISSUE | COMPLETED | VIGNESH | 1
PASONS | 28 | FUJ | VEG CHILLER HIGH TEMP | COMPLETED | VIGNESH | 4
PASONS | FUJAIRAH | FUJ | COMPRESSOR REPLACEMNET | ATTENDED | SABITH ALI | 2
PASONS | FUJAIRAH | FUJ | COMPROSSER INSTALATION | COMPLETED | SABITH ALI | 2
PASONS | FUJAIRAH | FUJ | CONDENSSOR FAN MOTOR CHANGE - 1 NOS 350MM | COMPLETED | SABITH ALI | 1
PASONS | FUJAIRAH | FUJ | JUICE CHILLER HIGH TEMP | ATTENDED | VIGNESH | 1
PASONS | FUJEIRAH | FUJ | FREEZER BACK STORE COLD ROOM FAN NOT WORKING | ATTENDED | RACEL | 1
PASONS | FUJEIRAH | FUJ | COLD ROOM HIGH TEMP | COMPLETED | SABITH ALI | 1
PHD | ABU DHABI | AUH | Q3 PPM FINISHED | COMPLETED | FROILAN | 37
RNQ | AJMAN | AJM | COLD ROOM TEMP. ISSUE | COMPLETED | VIGNESH | 2
RNQ | AJMAN | AJM | COLD ROOM TEMP. ISSUE | NOT ATTENDED | VIGNESH | 2
RNQ | AJMAN | AJM | PPM | COMPLETED | BIJU | 37
RNQ | AJMAN | AJM | UNIT TRIPPING ISSUE | (blank) | (blank) | 1
STELLAR OCEAN | AL QUOZ | DXB | FREEZER COLD ROOM NOT WORKING | COMPLETED | SARAVANAN | 1
TCS | 1057 | DXB | VERTICAL FREEZER ICE FORMATION | ATTENDED | SADAM | 2
TCS | AL AWEER | DXB | PPM | COMPLETED | SUDHEESH | 37
TCS | AL AWEER | DXB | WATER PIPE LINE BLOCK AND LEAKAGE OF WATER IN CHILLER NO 48 | COMPLETED | SADAM | 1
TCS | AL AWEER | DXB | CHILLER NO 46 NOT WORKING TRIPPING ISSUE | COMPLETED | SARAVANAN | 1
TCS | AL RAIS | DXB | DISPLAY FREEZER AND FREEZER COLD ROOM ICE FORMATION | ATTENDED | RACEL | 1
TCS | BAY SQUARE | DXB | PORK SECTION CHILLER 1 LIGHT NOT WORKING | ATTENDED | SADAM | 1
TCS | DARWISH HAMDAN | AUH | FREEZER UNIT ICE FORMATION | COMPLETED | OLIVER | 1
TCS | DEC MARINA | DXB | BACK STORE FREEZER TEMP ISSUE / ICE CREAM FREEZER CABINET WATER LEAK | COMPLETED | SARAVANAN | 4
TCS | DEC MARINA | DXB | DISPLAY FREEZER NOT WORKING | ATTENDED | RACEL | 1
TCS | DEC MARINA | DXB | FREEZER WATER LEAK | ATTENDED | SARAVANAN | 2
TCS | DEC MARINA | DXB | FREEZER WATER LEAK | COMPLETED | SARAVANAN | 2
TCS | EMERALD COURT | DXB | ICE MACHINE HAS SHUT DOWN | COMPLETED | SADAM | 1
TCS | EMERALD COURT | DXB | ICE MACHINE NOT WORKING | COMPLETED | MOHAMMED | 1
TCS | EMERALD COURT | DXB | PORK FREEZER WATER LEAK | COMPLETED | SADAM | 1
TCS | FALCON KHALIDIYA | AUH | BAKERY CHILLER DISPLAY HIGH TEMP FREEZER CABINET HIGH TEMP (CHICKEN SECTION) | ATTENDED | OLIVER | 1
TCS | FALCON KHALIDIYA | AUH | BAKERY CHILLER HIGH TEMP / FISH SECTION CHILLER | ATTENDED | FROILAN | 1
TCS | FALCON KHALIDIYA | AUH | BAKERY CHILLER NOT WORKING | ATTENDED | RANDOLPH | 1
TCS | FALCON KHALIDIYA | AUH | COLD ROOM DOOR ICE FORMATION | COMPLETED | RANDOLPH | 1
TCS | FALCON KHALIDIYA | AUH | F&V CHILLER HIGH TEMP | COMPLETED | FROILAN, OLIVER | 1
TCS | FALCON KHALIDIYA | DXB | CHILLER HIGH TEMP | COMPLETED | FROILAN | 1
TCS | GREENS | DXB | STEEL BODY CHILLER HIGH TEMP / CHILLER WATER LEAK | ATTENDED | SHAFI | 1
TCS | GREENS | DXB | CHILLER WATER LEAK | COMPLETED | SADAM | 1
TCS | JULPHAR TOWER | RAK | DISPLAY FREEZER#5 ICE CREAM INSUFFICIENT COOLING | COMPLETED | DENNIS | 1
TCS | JULPHAR TOWER | RAK | FREEZER CABINET HIGH TEMP | ATTENDED | SARAVANAN | 1
TCS | JVC MANHATTAN | DXB | BAKERY CHILELR WATER LEAK | ATTENDED | RACEL | 1
TCS | JVC MANHATTAN | DXB | BSEMENT PARKING AREA NOISE ISSUE | ATTENDED | SHAFI | 1
TCS | JVC MANHATTAN | DXB | FREEZER WATER LEAK | COMPLETED | SHAFI | 1
TCS | JVC MANHATTAN | DXB | FREEZER WATER LEAKAGE | ATTENDED | SADAM | 1
TCS | KHALIDIYA | AUH | F&V NOT WOKRING | COMPLETED | RANDOLPH | 1
TCS | LAKES | DXB | CHILELR COLD ROOM TEMP ISSUE | ATTENDED | SARAVANAN | 2
TCS | LAKES | DXB | CHILELR COLD ROOM TEMP ISSUE | COMPLETED | SARAVANAN | 2
TCS | LAKES | DXB | CHILLER HIGH TEMP | ATTENDED | SHAFI | 1
TCS | LAKES | DXB | PORK SECTION CHILLER HIGH TEMP | COMPLETED | SHAFI | 1
TCS | LE GRAND | DXB | UNIT IN CONTINOUS DEFROST | ATTENDED | SADAM | 1
TCS | PALM SHORELINE | DXB | PPM | COMPLETED | GOVIND | 37
TCS | ROVE CITY CENTER | DXB | CHILLER HIGH TEMP | ATTENDED | SADAM | 1
TCS | ROVE CITY CENTER | DXB | FREEZER LIGHT NOT WORKING / CHILELR WTAER LEAK | ATTENDED | MOHAMMED | 1
TCS | ROVE CITY CENTER | DXB | WATER LEAK IN CHILLER | COMPLETED | SADAM | 1
TCS | ROVE DOWNTOWN | DXB | FREEZER NOISE ISSUE | ATTENDED | SHAFI | 1
TCS | ROVE DOWNTOWN | DXB | BAKERY CHILLER HIGH TEMP. | COMPLETED | MOHAMMED | 1
TCS | ROVE DOWNTOWN | DXB | FREEZER CABINET TEMP.ISSUE | ATTENDED | MOHAMMED | 2
TCS | ROVE DOWNTOWN | DXB | FREEZER CABINET TEMP.ISSUE/CHANGING COMPRESSOR | COMPLETED | SARAVANAN | 2
TCS | ROVE DOWNTOWN | DXB | FREZEER TEMP ISSUE | (blank) | (blank) | 1
TCS | ROVE DOWNTOWN | DXB | CHILLER WATER LEAK | COMPLETED | SARAVANAN | 1
TCS | ROVE HEALTH CARE | DXB | WATER LEAK | COMPLETED | MOHAMMED | 1
TCS | ROVE HEALTH CARE | DXB | WATER LEAKAGE FROM CHILLER | COMPLETED | SARVANAN | 1
TCS | ROVE TRADE CENTER | DXB | CHILLERS HIGH TEMP.ISSUE. | ATTENDED | SARAVANAN | 2
TCS | ROVE TRADE CENTER | DXB | CHILLERS HIGH TEMP.ISSUE. | ATTENDED | SABITH ALI | 2
TCS | RP HEIGHT | DXB | DAIRY CHILLER HAS ICE FORMATION | COMPLETED | MOHAMMED | 1
TCS | SAFA PARK | DXB | DISPLAY FREEZER NOT WORKING | ATTENDED | MOHAMMED | 1
TCS | SAFA PARK | DXB | DISPLAY FREEZER NOT WORKING | COMPLETED | SHAFI | 1
TCS | SAFA PARK | DXB | FREEZER HIGH TEMP | ATTENDED | SHAFI | 1
TCS | SHOROOQ | DXB | BAKERY FREEZER COLD ROOM NOT WORKING | COMPLETED | AHSAN | 1
TCS | SHOROOQ | DXB | BEVERAGE, DAIRY, F&v AND BAKERY CHILLER IS NOT FUNCTIONING | COMPLETED | VIGNESH | 1
TCS | SHOROOQ | DXB | FISH CHILLER NOT WORKING | COMPLETED | SARAVANAN | 1
TCS | UMS | DXB | CHILLER WATER LEAK | COMPLETED | MOHAMMED | 1
TCS | UMS | DXB | F & V CHILLER NOT WORKING | COMPLETED | VIGNESH | 2
TCS | UMS | DXB | FISH DISPLAY CHILLER WATER LEAKAGE | COMPLETED | SADAM | 1
TCS | UMS | DXB | FREEZER COLD ROOM AND FREEZER CABINET HIGH TEMP ISSUE / OPEN CHILLER NOT WORKING | ATTENDED | SARAVANAN | 1
TCS | UMS | DXB | FREEZER HIGH TEMP | COMPLETED | SADAM | 2
TCS | UMS | DXB | FREEZER TEMP. ISSUE | COMPLETED | SADAM | 1
TCS | UMS | DXB | FREEZER WATER LEAK | ATTENDED | MOHAMMED | 1
TCS | UMS | DXB | ICE CREAM FR5EEZER HIGH TEMP | COMPLETED | SARAVANAN | 1
TCS | UMS | DXB | ICE FORMATION IN DEI CHILLER AND MEAT BACKSTORE HIGH TEMP. | COMPLETED | SADAM | 1
TCS | UMS | DXB | ICECREAM FREEZER NOT WORKING | ATTENDED | MOHAMMED | 1
TCS | UMS | DXB | PORK FREEZER DIGITAL DISPLAY DAMAGE | ATTENDED | MOHAMMED | 1
TCS | UMS | DXB | PORK FREEZER TEMP ISSUE | COMPLETED | VIGNESH | 1
TCS | UMS | DXB | TRIPPING UNIT AND WEIGHING SCALE | ATTENDED | MOHAMMED | 1
TCS | UMS | DXB | VEG & FRUIT CHILLER NOT WORKING | ATTENDED | MOHAMMED | 2
TCS | UMS | DXB | BACK STORE ROOM TEMP. ISSUE | COMPLETED | VIGNESH | 1
TCS | UMS | DXB | PLUG IN CHILLER NOT WORKING | COMPLETED | SHABEEB | 1
TCS | UMS | DXB | BACKERY SECTION TEMP. ISSUE | COMPLETED | SHABEEB | 1
WESTLAND | AL AIN | AL AIN | CHILLER CDU ICE FORMATION IN PIPE LINE | ATTENDED | SHAFI | 3
WESTLAND | AL AIN | AL AIN | CHILLER UNIT NOT WORKING | COMPLETED | TALIB | 1
WESTLAND | AL AIN | AL AIN | GENERAL VISIT | COMPLETED | TALIB | 1
WESTLAND | AL AIN | AL AIN | NO.05 UNIT ICE FORMATION | COMPLETED | AHSAN | 3
WESTLAND | AL AIN | AL AIN | OBSERVATION ALL CHILLER UNITS | COMPLETED | TALIB | 37
WESTLAND | AL AIN | AL AIN | OUT DOOR ICE FORMATION | COMPLETED | TALIB | 1
WESTLAND | AL AIN | AL AIN | GLASS CHILLER CONDENSOR LEAK | COMPLETED | TALIB | 1
WESTLAND | AL AIN | AL AIN | OUTDOOR UNIT ACCUMULATOR ICE FORMATION / PREPARATION ROOM LOW COOLING | ATTENDED | TALIB | 3
WESTLAND | AL AIN | AL AIN | OLD UNIT NOT WORKING PROPERLY | COMPLETED | TALIB | 1
WESTLAND | AL AIN | AL AIN | VISUAL CHECK | COMPLETED | TALIB | 1
(blank) | (blank) | DXB | DRIVING | COMPLETED | MOHAMMED | 27
(blank) | (blank) | DXB | DRIVING | COMPLETED | WILSON | 28
(blank) | (blank) | (blank) | DRIVING | ATTENDED | WILSON | 27
(blank) | (blank) | (blank) | DRIVING | COMPLETED | GOVINTH | 27
(blank) | (blank) | (blank) | DRIVING | COMPLETED | WILLSON | 54
(blank) | (blank) | (blank) | DRIVING | COMPLETED | WILSON | 513
(blank) | (blank) | (blank) | DRIVING | COMPLETED | WISLON | 0
(blank) | (blank) | (blank) | DRIVING | COMPLETED | WILSON | 54
(blank) | (blank) | (blank) | (blank) | (blank) | (blank) | 0
(blank) | DRIVING | DXB | DRIVING | COMPLETED | WILSON | 3
COLOURS EXPRESS | SUPER MARKET | AUH | DRINKS CHILLER NOT WORKING | COMPLETED | RANDOLPH | 1
COLOURS EXPRESS | SUPER MARKET | AUH | CHILLER NOT WORKING | ATTENDED | RANDOLPH | 1
BLUE WATER MARINA | BANIYA FOREST | DXB | PPM | COMPLETED | SARAVANAN | 1
TD | DRIVING | DXB | DRIVING | COMPLETED | WILSON | 1
77 TEXAS BBQ | SILICON OASSIS | DXB | PPM | COMPLETED | SARAVANAN | 1
FLOWE SHOP | DUBAI | DXB | MONOBLOCK INSTALATION | COMPLETED | DENNIS/MOHAMMED | 1
SWEET CONNECTION | DIP | DXB | FREEZER NOISE ISSUE | COMPLETED | SADAM | 1
WAHAT AL MASA | RICE WAREHOUSE | AUH | 10 UNITS NEED TO CHECK TEMP. | ATTENDED | RANDOLPH/TROVEE | 1
BANYA FOREST | BLUE WATER | DXB | AC NOT WORKING | COMPLETED | SADAM | 1
BANYA FOREST | DUBAI | DXB | KITCHRN AC ISSUE | ATTENDED | ABUTAKHIR | 1
MAMZAR VILLA | DUBAI | DXB | FREEZER COLD ROOM NOT WORKING | COMPLETED | SADAM | 1
PASSONS | FUJEIRAH | FUJ | DELI CHILLER TRIPPING | COMPLETED | VIGNESH | 1
PASSONS | FUJEIRAH | FUJ | BUTCHRY SECTION DISPLAY CHILLER TEMP ISSUE | COMPLETED | SABITH ALI | 1
CAREEM | AL QUOZ | DXB | PPM | COMPLETED | ABHIJITH | 1
CAREEM | JVC PLAZA | DXB | CHILLER HIGH TEMP. ISSUE | ATTENDED | VIGNESH | 1
LINDE HELIUM | JABAL ALI PORT | DXB | GAS CHARGING | COMPLETED | AHSAN | 1
ASWAQ | KHALIFA CITY | RAK | PPM | COMPLETED | SUDHEESH | 1
ASWAQ | GHALILAH | RAK | FROZEN FREEZER NOT WORKING | ATTENDED | AHSAN | 1
ASWAQ | AL DHAITH | RAK | DELI COUNTER CH 03 TEMP ISSUE / BUTCHERY COUNTER CHILLER SH 37 TEMP ISSUE | COMPLETED | AHSAN | 1
ASWAQ | AL DHAITH | RAK | WALKIN FREEZER ISSUE | (blank) | (blank) | 1
ASWAQ | SOUTH AL DAITH | RAK | CHILLER CABINET HIGH TEMP | ATTENDED | RACEL | 1
HYPERMAX | 360 MALL | KWT | PPM CABINET CLEANING | COMPLETED | RAUL | 1
HYPERMAX | CITY CENTER | OMR | PPM IN DELI CHILLER | COMPLETED | MOHAMMAD SHANTA | 1
HYPERMAX | CITY CENTER | OMR | MEET SECTION CHILLER NOT COOLING | COMPLETED | MOHAMMAD SHANTA | 1
HYPERMAX | SALALAH | OMR | DELI CHILLER WATER LEAKAGE ISSUE | COMPLETED | ALISON | 1
HYPERMAX | SALALAH | OMR | MINUS RANGE COMPRESSOR NO 2 TRIPPING ISSUE | ATTENDED | ALISON | 1

## CALLS PER TECH
DATE | (All)
Row Labels | No. of calls attended
RANDOLPH | 134
SADAM | 127
SARAVANAN | 118
VIGNESH | 100
AHSAN | 98
MOHAMMED | 96
RACEL | 86
OLIVER | 68
SHAFI | 63
TALIB | 45
FROILAN | 44
WILSON | 30
MUTHUKUMAR | 18
SHABEEB | 18
SARVANAN | 17
TROVEE | 16
BIJU | 14
ABID | 10
ROGER | 9
SUDHEESH | 7
ABID, AJMEER | 6
GOVIND | 6
ABHIJITH | 5
MUSTAFA | 4
DENNIS, ROGER | 4
FROILAN, OLIVER | 3
ROGER | 3
SHAFI, DENNIS | 2
DENNIS | 2
WILLSON | 2
SELVAN | 2
ALLAN | 2
ZALAUDDIN | 2
RACEL/MOHAMMED/SARAVANAN | 2
SHAFI, SABITH, SARAVANAN | 1
RAJESH | 1
VIGNESH | 1
GOVINTH | 1
BIJU, LORIMER | 1
GOVIND | 1
OILVER | 1
SHABIB | 1
IN HOUSE TEAM | 1
RANDOLPH, TROVEE, OLIVER | 1
DENNIS | 1
FROILAN | 1
SHABAN | 1
RANDOLPH, TROVEE | 1
VIGNESH, SELVAN, SUDHEESH | 1
DENNIS, SHAFI, SABITH | 1
SHAFI | 1
DENNIS, SHAFI | 1
ROGER, GOVIND | 1
SHAFI/DENNIS | 1
DENNIS, MUTHUKUMAR | 1
Grand Total | 1184

## WORKSHEET
SL.NO | CUSTOMER | BRANCH | LOCATION | FAILURE DETAILS | Status | TECH 1
1 | AD COOP/DEYAAR | MEGAMART QASSIMIYA | SHJ | FROZEN FREEZER NOT WORKING | ATTENDED | SABITH ALI
2 | AD COOP/DEYAAR | MUROOR | AUH | BUTCHERY COLD ROOM MONOBLOCK ICE FORMATION | ATTENDED | FROILAN
3 | AD COOP/DEYAAR | SPAR SAADIAYT | AUH | CHEESE SECTION SHUT DOWN | COMPLETED | RANDOLPH
4 | AMAZON | DXB 3 | DXB | PPM DONE Q 1 | COMPLETED | ABID
5 | BANIYAS COOP | SARAB | AUH | FREEZER COLD ROOM NOT WORKING | ATTENDED | RANDOLPH
6 | BANIYAS COOP | SHAHAMA | AUH | FREEZER TEMP.ISSUE AND SOUND IN UNIT | COMPLETED | FROILAN
7 | BANIYAS COOP | SHAHAMA | AUH | CHILLER TEMP ISSUE./EGG CHILLER CHANGING COMPRESSOR | COMPLETED | RANDOLPH
8 | BAQER MOHEBI | ABU HAIL | SHJ | FREEZER LIGHT NOT WORKING | ATTENDED | AHSAN
9 | CAREEM | AL RAFFA | DXB | CHILLER DOOR FRAME BROKEN | ATTENDED | MOHAMMED
10 | CAREEM | JVT | DXB | FREEZER COLD ROOM HIGH TEMP | COMPLETED | MOHAMMED
11 | CAREEM | MOTOR CITY | DXB | CHILLER WATER LEAK AND DOOR ISSUE | ATTENDED | SADAM
12 | CAREEM | DIC | DXB | PPM DONE DUBAI INTERNET CITY STORE | COMPLETED | ZALAUDIN
13 | ENOC | 1031 | DXB | chiller pipe is leaking | COMPLETED | (blank)
14 | ENOC | 1033 | DXB | PPM | COMPLETED | BIJU,MUTHUKUMAR
15 | ENOC | 1035 | DXB | Walk in freezer not working | COMPLETED | SARVANAN
16 | ENOC | 1036 | DXB | Walk in freezer not working | ATTENDED | SADAM
17 | ENOC | 1052 | DXB | open chiller showing high temp 10.1 | COMPLETED | MOHAMMED
18 | ENOC | 1063 | DXB | Pronto display chiller air filter | NOT ATTENDED
19 | ENOC | 1079 | DXB | PPM | COMPLETED | BIJU
20 | ENOC | 1079 | DXB | Deli Counter Chiller light is not working | NOT ATTENDED
21 | ENOC | 1094 | DXB | walk in freezer ice formation in condens | COMPLETED | SADAM
22 | ENOC | 1204 | DXB | OPEN CHILLER TEMP ISSUE | NOT ATTENDED
23 | ENOC | 2020 | DXB | Pronto walk in freezer | COMPLETED | SADAM
24 | ENOC | 1047 | DXB | WALK-IN FREEZER | NOT ATTENDED
25 | ENOC | 1507 | DXB | Walking Chiller temperature abnormal | COMPLETED | VIGNESH
26 | ENOC | 1602 | DXB | VERTICAL FREEZER TEMP ISSUE | NOT ATTENDED
27 | GRANDIOSE | SOUQ AL BAHAR | DXB | NEED TO CHECK COMPRESSOR | COMPLETED | SARAVANAN
28 | HOP | JABAL ALI | DXB | FEMALE CHANGING ROOM AC NOT WORKING | NOT ATTENDED
29 | LULU | TERRACE MALL | KWT | PLUG IN FREEZER AN AND COLD ROOM BAKERY HIGH TEMP | COMPLETED | JOSE LITO
30 | NESTO | AJC | AJM | ICE MACHINE NOT WORKING | ATTENDED | AHSAN
31 | NESTO | AJE | AJM | BUTCHERY COLD ROOM MONOBLOCK WATER LEAKING | COMPLETED | AHSAN
32 | NESTO | AJJ | AJM | FREEZER TEMP. NORMAL BUT LOW AIR FLOW | COMPLETED | AHSAN
33 | NESTO | AJJ | AJM | CHILLER NO 1 NOT WORKING | COMPLETED | AHSAN
34 | NESTO | AJJ | AJM | BUTCHERY COUNTER NO 1 EVAPORATOR ICE AND CONTROLLER SHOWING ERROR | COMPLETED | AHSAN
35 | NESTO | MUWAILHA | SHJ | FREEZER COLD ROOM TEMP.ISSUE | COMPLETED | SABITH ALI
36 | TCS | AL AWEER | DXB | CHILLER NO 46 NOT WORKING TRIPPING ISSUE | COMPLETED | SARAVANAN
37 | TCS | ROVE DOWNTOWN | DXB | FREEZER CABINET TEMP.ISSUE/CHANGING COMPRESSOR | COMPLETED | SARAVANAN
38 | (blank) | DRIVING | DXB | DRIVING | COMPLETED | WILSON
39 | PASSONS | FUJEIRAH | FUJ | BUTCHRY SECTION DISPLAY CHILLER TEMP ISSUE | COMPLETED | SABITH ALI
40 | ASWAQ | KHALIFA CITY | RAK | PPM | COMPLETED | SUDHEESH
41 | HYPERMAX | CITY CENTER | OMR | MEET SECTION CHILLER NOT COOLING | COMPLETED | MOHAMMAD SHANTA
42 | HYPERMAX | SALALAH | OMR | MINUS RANGE COMPRESSOR NO 2 TRIPPING ISSUE | ATTENDED | ALISON
| CUSTOMER | BRANCH | Others Details/ Spare parts needed
| HYPERMAX | SALALAH | NEED:- OIL CHARGE
| BANIYAS COOP | SARAB | NEED:- ROCKER SWITCH - 1PCS
| BAQER MOHEBI | ABU HAIL | NEED:- TUBE LIGHTS
| CAREEM | MOTOR CITY | NEED:- SLIDING HOLDER - 1 SET
| NESTO | AJC | NEED:- RUBBER ANTI VIBRATION BUSH - 1 NOS .
| AD COOP/DEYAAR | MEGAMART QASSIMIYA | NEED:- FLEXIBLE DRAIN PIPE - 1 MTR
| AD COOP/DEYAAR | MUROOR | NEED:-HEATER ROD STRAIGHT-2PCS
| TCS | ROVE DOWNTOWN | USED:- NT2170U COMPRESSORE AND INSTATATION ITEMS
| CAREEM | JVT | USED:- SOLENOID COIL - 1 NOS BY TD
| CAREEM | AL RAFFA | NEED:- CAREL CONTROLLER AND SENSOR
| BANIYAS COOP | SHAHAMA | USED :- EMBRACO COMPRESSOR AND INSTALATION MATERIALS
| NESTO | AJJ | USED:- SOLENOID COIL - 1 NOS BY TD
| CUSTOMER | BRANCH | Others Details/ Spare parts needed
| ENOC | 2020 | USED:- 16 W FAN MOTOR - 1 NOS BY TD
| ENOC | 1036 | NEED:- 3/4 COPPER PIPE - 1 MTR ,R 404 GAS - 2 NOS,SL 32 - 1 GALLON

## pivot data
DATE | (All) |  | CUSTOMER | (All)
Row Labels | Call Status |  |  | Column Labels
ATTENDED | 422 |  |  | ATTENDED | COMPLETED | NOT ATTENDED | Grand Total
COMPLETED | 899 |  | Calls per customer | 422 | 899 | 48 | 1369
NOT ATTENDED | 48
Grand Total | 1369
|  | Technician | (All)
(All) |  |  | Column Labels
|  |  | ATTENDED | COMPLETED | Grand Total
|  | Count of TD REPORT NO. | 422 | 899 | 1321

## dashboard
CALL STATUS
ATTENDED | 422
COMPLETED | 899
NOT ATTENDED | 48
Timeline: Works in Excel 2013 or higher. Do not move or resize.